## Schedules - Assembly (hidden)
Hour of Day (Time) | Schedule for Occupancy |  |  | Schedule for Lighting/Receptacle |  |  | Schedule for HVAC System |  |  | Schedule for Service Hot Water |  |  | Schedule for Elevator
| Percent of Maximum Load |  |  | Percent of Maximum Load | [5 empty] | Percent of Maximum Load |  |  | Percent of Maximum Load
| Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun
1 (12-1am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 0 | 0 | 0 | 0 | 0 | 0
2 (1-2am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 0 | 0 | 0 | 0 | 0 | 0
3 (2-3am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 0 | 0 | 0 | 0 | 0 | 0
4 (3-4am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 0 | 0 | 0 | 0 | 0 | 0
5 (4-5am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 0 | 0 | 0 | 0 | 0 | 0
6 (5-6am) | 0 | 0 | 0 | 5 | 5 | 5 | On | Off | Off | 0 | 0 | 0 | 0 | 0 | 0
7 (6-7am) | 0 | 0 | 0 | 35/40 | 5 | 5 | On | On | On | 0 | 0 | 0 | 0 | 0 | 0
8 (7-8am) | 0 | 0 | 0 | 35/40 | 30 | 30 | On | On | On | 0 | 0 | 0 | 0 | 0 | 0
9 (8-9am) | 20 | 20 | 10 | 35/40 | 30 | 30 | On | On | On | 0 | 0 | 0 | 0 | 0 | 0
10 (9-10am) | 20 | 20 | 10 | 65/75 | 40/50 | 30 | On | On | On | 5 | 5 | 5 | 0 | 0 | 0
11 (10-11am) | 20 | 20 | 10 | 65/75 | 40/50 | 30 | On | On | On | 5 | 5 | 5 | 0 | 0 | 0
12 (11-12pm) | 80 | 60 | 10 | 65/75 | 40/50 | 30 | On | On | On | 35 | 20 | 10 | 0 | 0 | 0
13 (12-1pm) | 80 | 60 | 10 | 65/75 | 40/50 | 55/65 | On | On | On | 5 | 0 | 0 | 0 | 0 | 0
14 (1-2pm) | 80 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 5 | 0 | 0 | 0 | 0 | 0
15 (2-3pm) | 80 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 5 | 0 | 0 | 0 | 0 | 0
16 (3-4pm) | 80 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 5 | 0 | 0 | 0 | 0 | 0
17 (4-5pm) | 80 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 5 | 0 | 0 | 0 | 0 | 0
18 (5-6pm) | 80 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 0 | 0 | 0 | 0 | 0 | 0
19 (6-7pm) | 20 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 0 | 0 | 0 | 0 | 0 | 0
20 (7-8pm) | 20 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 0 | 65 | 65 | 0 | 0 | 0
21 (8-9pm) | 20 | 60 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 0 | 30 | 30 | 0 | 0 | 0
22 (9-10pm) | 20 | 80 | 70 | 65/75 | 40/50 | 55/65 | On | On | On | 0 | 0 | 0 | 0 | 0 | 0
23 (10-11pm) | 10 | 10 | 20 | 25 | 40/50 | 55/65 | On | On | On | 0 | 0 | 0 | 0 | 0 | 0
24 (11-12am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 0 | 0 | 0 | 0 | 0 | 0
Total/Day | 710 | 750 | 700 | 1010/1155 | 660/800 | 745/845 | 1800 | 1700 | 1700 | 70 | 125 | 115 | 0 | 0 | 0
Total/Week | 50 |  |  | 64.55/74.2 |  |  | 124 |  |  | 5.9 |  |  | 0
Total/Year | 2607 |  |  | 3357/3869 |  |  | 6465.36 |  |  | 307.626 |  |  | 0

## Schedules - Office (hidden)
Hour of Day (Time) | Schedule for Occupancy |  |  | Schedule for Lighting/Receptacle |  |  | Schedule for HVAC System |  |  | Schedule for Service Hot Water |  |  | Schedule for Elevator
| Percent of Maximum Load |  |  | Percent of Maximum Load | [5 empty] | Percent of Maximum Load |  |  | Percent of Maximum Load
| Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun
1 (12-1am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 5 | 4 | 0 | 0 | 0
2 (1-2am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 5 | 4 | 0 | 0 | 0
3 (2-3am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 5 | 4 | 0 | 0 | 0
4 (3-4am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 5 | 4 | 0 | 0 | 0
5 (4-5am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 5 | 4 | 0 | 0 | 0
6 (5-6am) | 0 | 0 | 0 | 10 | 5 | 5 | Off | Off | Off | 8 | 8 | 7 | 0 | 0 | 0
7 (6-7am) | 10 | 10 | 5 | 10 | 10 | 5 | On | On | Off | 7 | 7 | 4 | 0 | 0 | 0
8 (7-8am) | 20 | 10 | 5 | 30 | 10 | 5 | On | On | Off | 19 | 11 | 4 | 35 | 16 | 0
9 (8-9am) | 95 | 30 | 5 | 65/95 | 30 | 5 | On | On | Off | 35 | 15 | 4 | 69 | 14 | 0
10 (9-10am) | 95 | 30 | 5 | 65/95 | 30 | 5 | On | On | Off | 38 | 21 | 4 | 43 | 21 | 0
11 (10-11am) | 95 | 30 | 5 | 65/95 | 30 | 5 | On | On | Off | 39 | 19 | 4 | 37 | 18 | 0
12 (11-12pm) | 95 | 30 | 5 | 65/95 | 30 | 5 | On | On | Off | 47 | 23 | 6 | 43 | 25 | 0
13 (12-1pm) | 50 | 10 | 5 | 55/80 | 15 | 5 | On | On | Off | 57 | 20 | 6 | 58 | 21 | 0
14 (1-2pm) | 95 | 10 | 5 | 65/95 | 15 | 5 | On | On | Off | 54 | 19 | 9 | 48 | 13 | 0
15 (2-3pm) | 95 | 10 | 5 | 65/95 | 15 | 5 | On | On | Off | 34 | 15 | 6 | 37 | 8 | 0
16 (3-4pm) | 95 | 10 | 5 | 65/95 | 15 | 5 | On | On | Off | 33 | 12 | 4 | 37 | 4 | 0
17 (4-5pm) | 95 | 10 | 5 | 65/95 | 15 | 5 | On | On | Off | 44 | 14 | 4 | 46 | 5 | 0
18 (5-6pm) | 30 | 5 | 5 | 35/50 | 5 | 5 | On | On | Off | 26 | 7 | 4 | 62 | 6 | 0
19 (6-7pm) | 10 | 5 | 0 | 30 | 5 | 5 | On | Off | Off | 21 | 7 | 4 | 20 | 0 | 0
20 (7-8pm) | 10 | 0 | 0 | 30 | 5 | 5 | On | Off | Off | 15 | 7 | 4 | 12 | 0 | 0
21 (8-9pm) | 10 | 0 | 0 | 20 | 5 | 5 | On | Off | Off | 17 | 7 | 4 | 4 | 0 | 0
22 (9-10pm) | 10 | 0 | 0 | 20 | 5 | 5 | On | Off | Off | 8 | 9 | 7 | 4 | 0 | 0
23 (10-11pm) | 5 | 0 | 0 | 10 | 5 | 5 | Off | Off | Off | 5 | 5 | 4 | 0 | 0 | 0
24 (11-12am) | 5 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 5 | 4 | 0 | 0 | 0
Total/Day | 920 | 200 | 60 | 800/1040 | 280 | 120 | 1600 | 1200 | 0 | 537 | 256 | 113 | 555 | 151 | 0
Total/Week | 48.6 |  |  | 44.00/56.00 |  |  | 92 |  |  | 30.54 |  |  | 29.26
Total/Year | 2534.004 |  |  | 2288/2920 |  |  | 4796.88 |  |  | 1592.3556 |  |  | 1525.6164

## Schedules - Retail (hidden)
Hour of Day (Time) | Schedule for Occupancy |  |  | Schedule for Lighting/Receptacle |  |  | Schedule for HVAC System |  |  | Schedule for Service Hot Water |  |  | Schedule for Elevator
| Percent of Maximum Load |  |  | Percent of Maximum Load | [5 empty] | Percent of Maximum Load |  |  | Percent of Maximum Load
| Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun | Wk | Sat | Sun
1 (12-1am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 4 | 11 | 7 | 0 | 0 | 0
2 (1-2am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 10 | 7 | 0 | 0 | 0
3 (2-3am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 5 | 8 | 7 | 0 | 0 | 0
4 (3-4am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 4 | 6 | 6 | 0 | 0 | 0
5 (4-5am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 4 | 6 | 6 | 0 | 0 | 0
6 (5-6am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 4 | 6 | 6 | 0 | 0 | 0
7 (6-7am) | 0 | 0 | 0 | 5 | 5 | 5 | On | On | Off | 4 | 7 | 7 | 0 | 0 | 0
8 (7-8am) | 10 | 10 | 0 | 20 | 10 | 5 | On | On | Off | 15 | 20 | 10 | 12 | 9 | 0
9 (8-9am) | 20 | 20 | 0 | 50 | 30 | 10 | On | On | On | 23 | 24 | 12 | 22 | 21 | 0
10 (9-10am) | 50 | 50 | 10 | 85/90 | 55/60 | 10 | On | On | On | 32 | 27 | 14 | 64 | 56 | 11
11 (10-11am) | 50 | 60 | 20 | 85/90 | 85/90 | 40 | On | On | On | 41 | 42 | 29 | 74 | 66 | 13
12 (11-12pm) | 70 | 80 | 20 | 85/90 | 85/90 | 40 | On | On | On | 57 | 54 | 31 | 68 | 68 | 35
13 (12-1pm) | 70 | 80 | 40 | 85/90 | 85/90 | 55/60 | On | On | On | 62 | 59 | 36 | 68 | 68 | 37
14 (1-2pm) | 70 | 80 | 40 | 85/90 | 85/90 | 55/60 | On | On | On | 61 | 60 | 36 | 71 | 69 | 37
15 (2-3pm) | 70 | 80 | 40 | 85/90 | 85/90 | 55/60 | On | On | On | 50 | 49 | 34 | 72 | 70 | 39
16 (3-4pm) | 80 | 80 | 40 | 85/90 | 85/90 | 55/60 | On | On | On | 45 | 48 | 35 | 72 | 69 | 41
17 (4-5pm) | 70 | 80 | 40 | 85/90 | 85/90 | 55/60 | On | On | On | 46 | 47 | 37 | 73 | 66 | 38
18 (5-6pm) | 50 | 60 | 20 | 85/90 | 85/90 | 40 | On | On | Off | 47 | 46 | 34 | 68 | 58 | 34
19 (6-7pm) | 50 | 20 | 10 | 55/60 | 50 | 20 | On | On | Off | 42 | 44 | 25 | 68 | 47 | 3
20 (7-8pm) | 30 | 20 | 0 | 55/60 | 30 | 5 | On | On | Off | 34 | 36 | 27 | 58 | 43 | 0
21 (8-9pm) | 30 | 20 | 0 | 50 | 30 | 5 | On | On | Off | 33 | 29 | 21 | 54 | 43 | 0
22 (9-10pm) | 0 | 10 | 0 | 20 | 10 | 5 | Off | On | Off | 23 | 22 | 16 | 0 | 8 | 0
23 (10-11pm) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 13 | 16 | 10 | 0 | 0 | 0
24 (11-12am) | 0 | 0 | 0 | 5 | 5 | 5 | Off | Off | Off | 8 | 13 | 6 | 0 | 0 | 0
Total/Day | 720 | 750 | 280 | 1060/1155 | 940/985 | 500/525 | 1500 | 1600 | 900 | 662 | 690 | 459 | 844 | 761 | 288
Total/Week | 46.3 |  |  | 67.40/70.85 |  |  | 100 |  |  | 44.59 |  |  | 52.69
Total/Year | 2414.082 |  |  | 3505/3694 |  |  | 5214 |  |  | 2324.9226 |  |  | 2747.2566

## Schedules - Dwelling Unit (hidden)
Hour of Day (Time) | Schedule for Occupancy |  |  | Schedule for Lighting/Receptacle |  |  | Daily Thermostat Schedule |  | Schedule for Service Hot Water
| Percent of Maximum Load |  |  | Percent of Maximum Load |  |  |  |  | Percent of Maximum Load
| Wk | Sat | Sun | Wk | Sat | Sun | Cooling | Heating | Wk | Sat | Sun
1 (12-1am) | 1.6 | 1.6 | 1.6 | 5 | 5 | 5 | 70 | 78 | 5 | 5 | 5
2 (1-2am) | 1.6 | 1.6 | 1.6 | 5 | 5 | 5 | 70 | 78 | 5 | 5 | 5
3 (2-3am) | 1.6 | 1.6 | 1.6 | 5 | 5 | 5 | 70 | 78 | 5 | 5 | 5
4 (3-4am) | 1.6 | 1.6 | 1.6 | 5 | 5 | 5 | 70 | 78 | 5 | 5 | 5
5 (4-5am) | 1.6 | 1.6 | 1.6 | 5 | 5 | 5 | 70 | 78 | 5 | 5 | 5
6 (5-6am) | 1.6 | 1.6 | 1.6 | 5 | 5 | 5 | 70 | 78 | 5 | 5 | 5
7 (6-7am) | 7.7 | 7.7 | 7.7 | 5 | 5 | 5 | 72 | 78 | 30 | 30 | 30
8 (7-8am) | 14 | 14 | 14 | 5 | 5 | 5 | 72 | 78 | 50 | 50 | 50
9 (8-9am) | 14 | 14 | 14 | 50 | 50 | 50 | 72 | 78 | 40 | 40 | 40
10 (9-10am) | 10.8 | 10.8 | 10.8 | 50 | 50 | 50 | 72 | 80 | 30 | 30 | 30
11 (10-11am) | 10.8 | 10.8 | 10.8 | 50 | 50 | 50 | 72 | 80 | 30 | 30 | 30
12 (11-12pm) | 10.8 | 10.8 | 10.8 | 50 | 50 | 50 | 72 | 80 | 35 | 35 | 35
13 (12-1pm) | 7.7 | 7.7 | 7.7 | 30 | 30 | 30 | 72 | 80 | 40 | 40 | 40
14 (1-2pm) | 7.7 | 7.7 | 7.7 | 50 | 50 | 50 | 72 | 80 | 35 | 35 | 35
15 (2-3pm) | 7.7 | 7.7 | 7.7 | 50 | 50 | 50 | 72 | 80 | 35 | 35 | 35
16 (3-4pm) | 7.7 | 7.7 | 7.7 | 50 | 50 | 50 | 72 | 78 | 30 | 30 | 30
17 (4-5pm) | 7.7 | 7.7 | 7.7 | 50 | 50 | 50 | 72 | 78 | 30 | 30 | 30
18 (5-6pm) | 10.8 | 10.8 | 10.8 | 50 | 50 | 50 | 72 | 78 | 50 | 50 | 50
19 (6-7pm) | 21.7 | 21.7 | 21.7 | 35 | 35 | 35 | 72 | 78 | 50 | 50 | 50
20 (7-8pm) | 21.7 | 21.7 | 21.7 | 5 | 5 | 5 | 72 | 78 | 40 | 40 | 40
21 (8-9pm) | 21.7 | 21.7 | 21.7 | 5 | 5 | 5 | 72 | 78 | 35 | 35 | 35
22 (9-10pm) | 21.7 | 21.7 | 21.7 | 5 | 5 | 5 | 72 | 78 | 45 | 45 | 45
23 (10-11pm) | 18.6 | 18.6 | 18.6 | 5 | 5 | 5 | 72 | 78 | 30 | 30 | 30
24 (11-12am) | 1.6 | 1.6 | 1.6 | 5 | 5 | 5 | 70 | 78 | 5 | 5 | 5
Total/Day | 234 | 234 | 234 | 580 | 580 | 580 |  |  | 670 | 670 | 670
Total/Week | 16.38 |  |  | 40.6 |  |  |  |  | 46.9
Total/Year | 854.0532 |  |  | 2116.884 |  |  |  |  | 2445.366

## SCA Instructions (hidden)
Complete the tabs from the standard EN-1 form. The ASHRAE 90.1-2013 ECB baseline should be used for the baseline case
1,2,3 Information
4. Purchased Energy Rates
5. Usage Summary
6a. Ext. Wall Areas
6c. Wall Types
6d. Interior LPD- Space Method (do not complete Bldg Method worksheet)
6e. Ext LPD, 6f. Process Equip.
Ext LPD Calculator
6g. Service HW
6i. HVAC Air-side (complete 1 spreadsheet for each system type, add tabs as needed)
6j. HVAC Water-side CHW (proposed design only)
6l. HVAC Water-side HW & Steam
Complete the SCA Tabs
WORKBOOK COLOR LEGEND
Do not edit: information
Do not edit: information from EN-1
Do not edit: formulas
User edit
The SCA ECM Summary tab only needs to be completed if additional measures, which are not included in the proposed design, have been modeled for evaluation. If no measures have been modeled, this tab does not need to be completed.
Complete the General Checklist and the Output Report Checklist
Most of the information is linked to the EN-1 form. The information for the GSG baseline needs to be input in the SCA-specific tabs.
Additional Air-side tabs may need to be created, based on the design.
Carbon emissions (TonCO2e) in "SCA Exec Summary", Cell C43, will need to be manually calculated for buildings purchasing utilities other than natural gas and electricity (steam, fuel oil, etc)
Carbon Factors (2024-2029 1253-C)
| Electric Grid | 0.08468 | tCO2e/MMBtu
| Natural Gas Carbon Factor | 0.05311 | tCO2e/MMBtu
| Fuel Oil #2 Carbon Factor | 0.07421 | tCO2e/MMBtu
| Fuel Oil #4 Carbon Factor | 0.07529 | tCO2e/MMBtu
| Fuel Oil #5 Carbon Factor | 0.07293 | tCO2e/MMBtu
| Fuel Oil #6 Carbon Factor | 0.0751 | tCO2e/MMBtu
| District Steam Carbon Factor | 0.04493 | tCO2e/MMBtu
Print the Teal SCA Tabs and include in the printed submission.

## Lists (hidden)
Non-Residential | [7 empty] | 40 | Yes | kW | # | kW
Residential | [8 empty] | No | kBtu/h | SQFT | W/SF
Semiheated
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated |  | Section 11 ECB | EF | kBTU/h | EER | Et
Nonmetal framing (all) | U-0.35 | U-0.35 | U-0.51 | Nonmetal framing (all) | U-0.57 | U-0.57 | U-1.22 |  | Appendix G PRM | SL | tons | SEER | Ec
Metal framing (fixed) | U-0.42 | U-0.42 | U-0.73 | Metal framing (fixed) | U-0.57 | U-0.57 | U-1.22 |  |  | Et | kW |  | AFUE
Metal framing (operable) | U-0.50 | U-0.50 | U-0.81 | Metal framing (operable) | U-0.57 | U-0.57 | U-1.22 |  |  | COP | Btuh |  | COP
Metal framing (entrance door) | U-0.77 | U-0.68 | U-0.77 | Metal framing (entrance door) | U-0.57 | U-0.57 | U-1.22 | [5 empty] | HSPF
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated
Nonmetal framing (all) | 0.4 | 0.4 | NR | Nonmetal framing (all) | 0.39 | 0.39 | NR | All Other | 0.58
Metal framing (fixed) | 0.4 | 0.4 | NR | Metal framing (fixed) | 0.39 | 0.39 | NR | Healthcare/hospital | 0.57
Metal framing (operable) | 0.4 | 0.4 | NR | Metal framing (operable) | 0.39 | 0.39 | NR | Hotel/motel | 0.62
Metal framing (entrance door) | 0.4 | 0.4 | NR | Metal framing (entrance door) | 0.39 | 0.39 | NR | Multifamily | 0.78
[8 empty] | Office | 0.58
Skylights | Non-Residential | Residential | Semiheated | Skylights | Non-Residential | Residential | Semiheated | Restaurant | 0.58
0% - 2.0% | U-0.50 | U-0.50 | U-1.15 | 0% - 2.0% | U-0.69 | U-0.58 | U-1.36 | Retail | 0.55
2.1%+ | U-0.50 | U-0.50 | U-1.15 | 2.1%+ | U-0.69 | U-0.58 | U-1.36 | School | 0.49
[8 empty] | Warehouse | 0.58
Skylights | Non-Residential | Residential | Semiheated | Skylights | Non-Residential | Residential | Semiheated
0% - 2.0% | 0.4 | 0.4 | NR | 0% - 2.0% | 0.49 | 0.36 | NR
2.1%+ | 0.4 | 0.4 | NR | 2.1%+ | 0.39 | 0.19 | NR | Grocery Store | 7
[8 empty] | Healthcare (hospital) | 21
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated | Hospital | 27
Insulation Entirely Above Deck | U-0.032 | U-0.032 | U-0.093 | Insulation Entirely Above Deck | U-0.063 | U-0.063 | U-0.218 | Hotel/motel (< 75 rooms) | 24
Metal Building | U-0.037 | U-0.037 | U-0.082 | Metal Building | ERROR | ERROR | ERROR | Hotel/motel (> 75 rooms) | 34
Attic and Other | U-0.021 | U-0.021 | U-0.034 | Attic and Other | ERROR | ERROR | ERROR | Multifamily
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated | Office (< 5000 ft2) | 19
Mass | U-0.104 | U-0.090 | U-0.58 | Mass | ERROR | ERROR | ERROR | Office (> 50,000 ft2) | 40
Metal Building | U-0.060 | U-0.050 | U-0.162 | Metal Building | ERROR | ERROR | ERROR | Office (5000 - 50,000 ft2) | 31
Steel-Framed | U-0.064 | U-0.064 | U-0.124 | Steel-Framed | U-0.124 | U-0.064 | U-0.124 | Other
Wood-Framed and Other | U-0.064 | U-0.064 | U-0.089 | Wood-Framed and Other | ERROR | ERROR | ERROR | Restaurant (full service) | 24
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated | Restaurant (quick service) | 34
Below-Grade Wall | C-0.119 | C-0.092 | C-1.140 | Below-Grade Wall | C-1.140 | C-1.140 | C-1.140 | Retail ( strip mall) | 20
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated | Retail (Stand alone) | 11
Mass | U-0.057 | U-0.051 | U-0.107 | Mass | ERROR | ERROR | ERROR | School (primary) | 22
Steel-Joist | U-0.038 | U-0.038 | U-0.052 | Steel-Joist | U-0.052 | U-0.038 | U-0.069 | School (secondary and university) | 22
Wood-Framed and Other | U-0.033 | U-0.033 | U-0.051 | Wood-Framed and Other | ERROR | ERROR | ERROR | Warehouse (nonrefrigerated) | 6
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated
Unheated | F-0.520 | F-0.520 | F-0.7300 | Unheated | F-0.520 | F-0.730 | F-0.7300
Heated | F-0.843 | F-0.688 | F-0.900 | Heated | ERROR | ERROR | ERROR
| Non-Residential | Residential | Semiheated |  | Non-Residential | Residential | Semiheated
Swinging | U-0.500 | U-0.500 | U-0.700 | Swinging | U-0.700 | U-0.700 | U-0.700
Nonswinging | U-0.500 | U-0.500 | U-1.450 | Nonswinging | U-1.450 | U-0.500 | U-1.450
System 1: VAV with PFP boxes | VAV
System 10: PTAC | Single-speed fan
System 11: Packaged rooftop AC | Single- or two-speed fan
System 2: VAV with reheat | VAV
System 3: Packaged VAV with PFP boxes | VAV
System 4: Packaged VAV with reheat | VAV
System 5: Two-pipe fan-coil | Single- or two-speed fan
System 6: Water-source HP | Single- or two-speed fan
System 7: Four-pipe fan-coil | Single- or two-speed fan
System 8: PTHP | Single-speed fan
System 9: Packaged rooftop HP | Single- or two-speed fan
Heated-only storage | System 9: Heating and Ventilation | Constant Volume
Nonresidential - < 3 floors and < 25,000 ft2 | System 3: PSZ-AC | Constant Volume
Nonresidential - < 5 floors and 25,000 - 150,000 ft2 | System 5: Packaged VAV with Reheat | VAV
Nonresidential - > 5 floors or > 150,000 ft2 | System 7: VAV with reheat | VAV
Nonresidential - 4-5 floors and < 25,000 ft2 | System 5: Packaged VAV with Reheat | VAV
Public Assembly < 120,000 ft2 | System 3: PSZ-AC | Constant Volume
Public Assembly > 120,000 ft2 | System 12: Single-zone, CV-HW | Constant Volume
Residential | System 1: PTAC | Constant Volume
Retail - < 2 floors | System 3: PSZ-AC | Constant Volume
| System 1: PTAC | Constant Volume
| System 12: Single-zone, CV-HW | Constant Volume
| System 3: PSZ-AC | Constant Volume
| System 3: PSZ-AC | Constant Volume
| System 3: PSZ-AC | Constant Volume
| System 5: Packaged VAV with Reheat | VAV
| System 5: Packaged VAV with Reheat | VAV
| System 7: VAV with reheat | VAV
| System 9: Heating and Ventilation | Constant Volume
All Others | Gas Storage Water Heater
Automotive facility | Gas Storage Water Heater
Convention center | Electric Resistance Storage Water Heater
Courthouse | Electric Resistance Storage Water Heater
Dining: bar lounge/leisure | Gas Storage Water Heater
Dining: cafeteria/fast food | Gas Storage Water Heater
Dining: family | Gas Storage Water Heater
Dormitory | Gas Storage Water Heater
Exercise center | Gas Storage Water Heater
Fire station | Gas Storage Water Heater
Gymnasium | Gas Storage Water Heater
Health-care clinic | Gas Storage Water Heater
Hospital | Gas Storage Water Heater
Hotel/Motel | Gas Storage Water Heater
Library | Electric Resistance Storage Water Heater
Manufacturing facility | Gas Storage Water Heater
Motion picture theater | Electric Resistance Storage Water Heater
Multifamily | Gas Storage Water Heater
Museum | Electric Resistance Storage Water Heater
Office | Electric Resistance Storage Water Heater
Parking garage | Electric Resistance Storage Water Heater
Penitentiary | Gas Storage Water Heater
Performing arts theater | Gas Storage Water Heater
Police station | Electric Resistance Storage Water Heater
Post office | Electric Resistance Storage Water Heater
Religious building | Electric Resistance Storage Water Heater
Retail | Electric Resistance Storage Water Heater
School/university | Gas Storage Water Heater
Sports arena | Gas Storage Water Heater
Town hall | Electric Resistance Storage Water Heater
Transportation | Electric Resistance Storage Water Heater
Warehouse | Electric Resistance Storage Water Heater
Workshop | Gas Storage Water Heater

## GSG LPD (hidden)
Space by Space Categories | Table 9.6.1 LPD (W/sf)
Atrium - first 40ft in height |  |  |  | Medium
Atrium - height above 40ft |  |  |  | Large
Audience/seating area - all other | 0.79
Audience/seating area - auditorium | 0.79
Audience/seating area - convention center | 0.82
Audience/seating area - exercise center | 0.43
Audience/seating area - gymnasium | 0.43
Audience/seating area - motion picture theater | 1.14
Audience/seating area - penitentiary | 0.43
Audience/seating area - performing arts theater | 2.43
Audience/seating area - religious building | 1.53
Audience/seating area - sports arena | 0.43
Audience/seating area - transportation facility | 0.54
Automotive | 0.67
Banking Activity Area | 1.38
Classroom/lecture/training - all other | 1.24
Classroom/lecture/training - penitentiary | 1.34
Computer Room | 1.24 | COMPUTER CLASSROOM IS | 1.24
Conference/meeting/multipurpose | 1.23
Confinement Cells | 1.1
Convention Center-Exhibit Space | 1.45
Copy/Print Room | 1.11 | WAS | 1.11
Corridor - all other | 0.66
Corridor - facility for visually impaired | 0.66
Corridor - hospital | 0.89
Corridor - manufacturing facility | 0.41
Courtroom | 1.72
Dining Area - all other | 0.65
Dining Area - Bar Lounge/Leisure Dining | 1.31
Dining Area - cafeteria/fast food | 0.65
Dining Area - facility for visually impaired | 0.65
Dining Area - Family Dining | 0.89
Dining Area - penitentiary | 0.65
Dormitory - living quarters | 0.51
Electrical/Mechanical | 0.95
Emergency Vehicle Garage | 0.56
Facility for Visually Impaired - in a chapel | 2.21
Facility for Visually Impaired - in a rec room/common living rm | 2.41
Fire station - sleeping quarters | 0.38
Food Preparation Area | 0.99 | WAS | 1.21
Guest Room | 0.91
Gymnasium/Exercise Center-Playing Area | 1.2
Gymnasium/Fitness Center - exercise area | 0.72
Healthcare facility - exam treatment room | 1.66
Healthcare facility - imaging room | 1.51
Healthcare facility - medical supply room | 0.74
Healthcare facility - nursery | 0.88
Healthcare facility - nurse's station | 0.71
Healthcare facility - Operating Room | 2.48
Healthcare facility - Patient Room | 0.62
Healthcare facility - Physical Therapy | 0.91
Healthcare facility - Recovery | 1.15
Laboratory - in or as a classroom | 1.28
Laboratory - other | 1.81
Laundry/Washing Area | 0.6
Library - Reading Area | 0.93
Library - Stacks | 1.71
Loading Dock, Interior | 0.47
Lobby - all other | 0.9
Lobby - Elevator | 0.64
Lobby - facility for visually impaired | 1.8
Lobby - Hotel | 1.06
Lobby - Motion Picture Theater | 0.59
Lobby - Performing Arts Theater | 2
Locker Room | 0.75
Lounge/Breakroom - all other | 0.73
Lounge/Breakroom - healthcare facility | 0.92
Manufacturing-Detailed Manufacturing | 1.29
Manufacturing-Equipment Room | 0.95
Manufacturing-Extra High Bay (>50ft floor to ceiling ht) | 1.05
Manufacturing-High Bay (25-50ft floor to ceiling ht) | 1.23
Manufacturing-Low Bay (<25ft floor to ceiling ht) | 1.19
Multifamily Dwelling Unit | 0.51
Museum-General Exhibition | 1.05
Museum-Restoration | 1.02
Office - Enclosed and < 250 sqft | 1.11 | WAS | 1.11
Office - Enclosed and > 250 sqft | 1.11 | WAS | 1.11
Office - Open Plan | 0.98 | LEFT AS-IS (PDF DIDN'T SPECIFY ENCLOSED OR OPEN)
Parking Area, Interior | 0.19
Performing Arts Theater - dressing room | 0.61
Pharmacy Area | 1.68
Post Office-Sorting Area | 0.94
Religious Buildings-Fellowship Hall | 0.64
Religious Buildings-Worship Pulpit, Choir | 1.53
Restroom - all other | 0.98
Restroom - visually impaired | 1.21
Retail-Dressing/Fitting Room | 0.71
Retail-Mall Concourse | 1.1
Sales Area | 1.3
Seating Area, General | 0.54
Sports Arena-Court Sports Area-Class 1 | 3.68
Sports Arena-Court Sports Area-Class 2 | 2.4
Sports Arena-Court Sports Area-Class 3 | 1.8
Sports Arena-Court Sports Area-Class 4 | 1.2
Stairwell | 0.69
Storage room - all other | 0.63
Storage room - hospital | 0.63
Storage room < 50 sqft | 0.63
Storage room < 50 sqft and < 1000 sqft | 0.63
Transportation facility - airport concourse | 0.36
Transportation facility - baggage/carousel area | 0.53
Transportation facility - terminal ticket counter | 0.8
Vehicular Maintenance Area | 0.067
Warehouse storage - medium to bulky, palletized items | 0.58
Warehouse storage - smaller, hand-carried items | 0.95
Workshop | 1.59

## Lighting Lookup (hidden)
Building Area Method Categories | Table 9.5.1 LPD (W/sf) |  | Space by Space Categories | Table 9.6.1 LPD (W/sf)
Automotive facility | 0.8 | 0.9 | Atrium - first 40ft in height
Convention center | 1.01 | 1.2 | Atrium - height above 40ft
Courthouse | 1.01 | 1.2 | Audience/seating area - all other | 0.43 | 0.9
Dining: bar lounge/leisure | 1.01 | 1.3 | Audience/seating area - auditorium | 0.63 | 0.9
Dining: cafeteria/fast food | 0.9 | 1.4 | Audience/seating area - convention center | 0.82 | 0.7
Dining: family | 0.95 | 1.6 | Audience/seating area - exercise center | 0.65 | 0.3
Dormitory | 0.57 | 1 | Audience/seating area - gymnasium | 0.65 | 0.4
Exercise center | 0.84 | 1 | Audience/seating area - motion picture theater | 1.14 | 1.2
Fire station | 0.67 | 1 | Audience/seating area - penitentiary | 0.28 | 0.7
Gymnasium | 0.94 | 1.1 | Audience/seating area - performing arts theater | 2.43 | 2.6
Health-care clinic | 0.9 | 1 | Audience/seating area - religious building | 1.53 | 1.7
Hospital | 1.05 | 1.2 | Audience/seating area - sports arena | 0.43 | 0.4
Hotel/Motel | 0.87 | 1.09 | Audience/seating area - transportation facility | 0.43 | 0.5
Library | 1.19 | 1.3 | Automotive | 0.067 | 0.7
Manufacturing facility | 1.17 | 1.17 | Banking Activity Area | 1.01 | 1.5
Motion picture theater | 0.76 | 1.2 | Classroom/lecture/training - all other | 1.24 | 1.4
Multifamily | 0.51 | 0.7 | Classroom/lecture/training - penitentiary | 1.34 | 1.3
Museum | 1.02 | 1.1 | Computer Room | 1.71 | 2.14
Office | 0.82 | 1 | Conference/meeting/multipurpose | 1.23 | 1.3
Parking garage | 0.21 | 0.3 | Confinement Cells | 0.81 | 0.9
Penitentiary | 0.81 | 1 | Convention Center-Exhibit Space | 1.45 | 1.3
Performing arts theater | 1.39 | 1.6 | Copy/Print Room | 0.72 | 0.9
Police station | 0.87 | 1 | Corridor - all other | 0.66 | 0.5
Post office | 0.87 | 1.1 | Corridor - facility for visually impaired | 0.92 | 1.15
Religious building | 1 | 1.3 | Corridor - hospital | 0.99 | 1
Retail | 1.26 | 1.5 | Corridor - manufacturing facility | 0.41 | 0.5
School/university | 0.87 | 1.2 | Courtroom | 1.72 | 1.9
Sports arena | 0.91 | 1.1 | Dining Area - all other | 0.65 | 0.9
Town hall | 0.89 | 1.1 | Dining Area - Bar Lounge/Leisure Dining | 1.07 | 1.4
Transportation | 0.7 | 1 | Dining Area - cafeteria/fast food | 0.65 | 0.9
Warehouse | 0.66 | 0.8 | Dining Area - facility for visually impaired | 2.65 | 3.32
Workshop | 1.19 | 1.4 | Dining Area - Family Dining | 0.89 | 2.1
|  |  | Dining Area - penitentiary | 0.96 | 1.3
|  |  | Dormitory - living quarters | 0.38 | 1.11
|  |  | Electrical/Mechanical | 0.42 | 1.5
|  |  | Emergency Vehicle Garage | 0.56 | 0.8
|  |  | Facility for Visually Impaired - in a chapel | 2.21 | 2.77
|  |  | Facility for Visually Impaired - in a rec room/common living rm | 2.41 | 3.02
|  |  | Fire station - sleeping quarters | 0.38 | 0.3
|  |  | Food Preparation Area | 1.21 | 1.2
|  |  | Guest Room | 0.91 | 1.14
|  |  | Gymnasium/Exercise Center-Playing Area | 1.2 | 1.4
|  |  | Gymnasium/Fitness Center - exercise area | 0.72 | 0.9
|  |  | Healthcare facility - exam treatment room | 1.66 | 1.5
|  |  | Healthcare facility - imaging room | 1.51 | 0.4
|  |  | Healthcare facility - medical supply room | 0.74 | 1.4
|  |  | Healthcare facility - nursery | 0.88 | 0.6
|  |  | Healthcare facility - nurse's station | 0.71 | 1
|  |  | Healthcare facility - Operating Room | 2.48 | 2.2
|  |  | Healthcare facility - Patient Room | 0.62 | 0.7
|  |  | Healthcare facility - Physical Therapy | 0.91 | 0.9
|  |  | Healthcare facility - Recovery | 1.15 | 0.8
|  |  | Laboratory - in or as a classroom | 1.43 | 1.4
|  |  | Laboratory - other | 1.81 | 1.4
|  |  | Laundry/Washing Area | 0.6 | 0.6
|  |  | Library - Reading Area | 1.06 | 1.2
|  |  | Library - Stacks | 1.71 | 1.7
|  |  | Loading Dock, Interior | 0.47 | 0.59
|  |  | Lobby - all other | 0.9 | 1.3
|  |  | Lobby - Elevator | 0.64 | 0.8
|  |  | Lobby - facility for visually impaired | 1.8 | 2.26
|  |  | Lobby - Hotel | 1.06 | 1.1
|  |  | Lobby - Motion Picture Theater | 0.59 | 1.1
|  |  | Lobby - Performing Arts Theater | 2 | 3.3
|  |  | Locker Room | 0.75 | 0.6
|  |  | Lounge/Breakroom - all other | 0.73 | 1.2
|  |  | Lounge/Breakroom - healthcare facility | 0.92 | 0.8
|  |  | Manufacturing-Detailed Manufacturing | 1.29 | 2.1
|  |  | Manufacturing-Equipment Room | 0.74 | 1.2
|  |  | Manufacturing-Extra High Bay (>50ft floor to ceiling ht) | 1.05 | 1.32
|  |  | Manufacturing-High Bay (25-50ft floor to ceiling ht) | 1.23 | 1.7
|  |  | Manufacturing-Low Bay (<25ft floor to ceiling ht) | 1.19 | 1.2
|  |  | Multifamily Dwelling Unit | 0.51 | 0.7
|  |  | Museum-General Exhibition | 1.05 | 1
|  |  | Museum-Restoration | 1.02 | 1.7
|  |  | Office - Enclosed and < 250 sqft | 1 | 1.1
|  |  | Office - Enclosed and > 250 sqft | 1 | 1.1
|  |  | Office - Open Plan | 0.9 | 1.1
|  |  | Parking Area, Interior | 0.19 | 0.2
|  |  | Performing Arts Theater - dressing room | 0.61
|  |  | Pharmacy Area | 1.68 | 1.2
|  |  | Post Office-Sorting Area | 0.94 | 1.2
|  |  | Religious Buildings-Fellowship Hall | 0.64 | 0.9
|  |  | Religious Buildings-Worship Pulpit, Choir | 1.53 | 2.4
|  |  | Restroom - all other | 0.98 | 0.9
|  |  | Restroom - visually impaired | 1.21 | 1.52
|  |  | Retail-Dressing/Fitting Room | 0.71 | 0.89
|  |  | Retail-Mall Concourse | 1.1 | 1.7
|  |  | Sales Area | 1.3 | 1.7
|  |  | Seating Area, General | 0.54 | 0.68
|  |  | Sports Arena-Court Sports Area-Class 1 | 3.68 | 4.61
|  |  | Sports Arena-Court Sports Area-Class 2 | 2.4 | 3.01
|  |  | Sports Arena-Court Sports Area-Class 3 | 1.8 | 2.26
|  |  | Sports Arena-Court Sports Area-Class 4 | 1.2 | 1.5
|  |  | Stairwell | 0.69 | 0.6
|  |  | Storage room - all other | 0.63 | 0.8
|  |  | Storage room - hospital | 0.63 | 0.9
|  |  | Storage room < 50 sqft | 1.24 | 0.8
|  |  | Storage room < 50 sqft and < 1000 sqft | 0.63 | 0.8
|  |  | Transportation facility - airport concourse | 0.36 | 0.6
|  |  | Transportation facility - baggage/carousel area | 0.53 | 1
|  |  | Transportation facility - terminal ticket counter | 0.8 | 1.5
|  |  | Vehicular Maintenance Area | 0.067 | 0.7
|  |  | Warehouse storage - medium to bulky, palletized items | 0.58 | 0.9
|  |  | Warehouse storage - smaller, hand-carried items | 0.95 | 1.4
|  |  | Workshop | 1.59 | 1.9

## Lighting Zones (hidden)
| Lighting Zone | Description | Base Site Allowance (watts)
1 | 0 | Undeveloped areas within national and state parks, forest land and rural areas and other undeveloped areas as approved by the AHJ | 0
2 | 1 | Park Land | 500
3 | 2 | R districts, R districts with C overlays and MX districts | 600
4 | 3 | M districts, except MX; C districts, except C5, C6 and C overlays on R | 750
5 | 4 | C5 and C6 districts | 1300
YES
NO

## Raw Data (hidden)
|  |  | Area Allowance (watts/sq.ft) |  |  |  |  | Linear Allowance (watts/linear foot) | [8 empty] | Area Allowance (watts/sq.ft) |  |  |  |  | Linear Allowance (watts/linear foot)
Surface | Surface Type | Type | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Base Allowance | Unit Allowance | Surface2 | Surface Type | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Base Allowance | Unit Allowance
ATM or Night Depository | Nontradable | 1 | [10 empty] | 270 | 90 | Uncovered parking areas and drives | Tradable | 0 | 0.04 | 0.06 | 0.1 | 0.13
Building façade | Nontradable |  | 0 | 0 | 0.1 | 0.15 | 0.2 | 0 | 0 | 2.5 | 3.75 | 5 |  |  | Walkways less than 10' wide | Tradable | [5 empty] | 0 | 0.7 | 0.7 | 0.8 | 1
Drive-thrus | Nontradable | [12 empty] | 400 | Walkways >= 10' wide | Tradable | 0 | 0.14 | 0.14 | 0.16 | 0.2
Entrances and gatehouse inspection at guarded facilities (uncovered) | Nontradable |  | 0 | 0.75 | 0.75 | 0.75 | 0.75 | [7 empty] | Plaza areas | Tradable | 0 | 0.14 | 0.14 | 0.16 | 0.2
Entry canopies | Tradable |  | 0 | 0.25 | 0.25 | 0.4 | 0.4 | [7 empty] | Special feature areas | Tradable | 0 | 0.14 | 0.14 | 0.16 | 0.2
Landscaping | Tradable |  | 0 | 0.04 | 0.05 | 0.05 | 0.05 | [7 empty] | Stairways | Tradable | 0 | 0.75 | 1 | 1 | 1
Loading area for emergency service vehicles (uncovered) | Nontradable |  | 0 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | Pedestrian tunnels | Tradable | 0 | 0.15 | 0.15 | 0.2 | 0.3
Loading docks | Tradable |  | 0 | 0.5 | 0.5 | 0.5 | 0.5 | [7 empty] | Landscaping | Tradable | 0 | 0.04 | 0.05 | 0.05 | 0.05
Other entrances/exits | Tradable | [6 empty] | 0 | 20 | 20 | 20 | 20 |  |  | Primary building entrances | Tradable | [5 empty] | 0 | 20 | 20 | 30 | 30
Outdoor sales area | Tradable |  | 0 | 0.25 | 0.25 | 0.5 | 0.7 | [7 empty] | Other entrances/exits | Tradable | [5 empty] | 0 | 20 | 20 | 20 | 20
Parking near 24-hour retail entrances (main only) | Nontradable | [12 empty] | 800 | Entry canopies | Tradable | 0 | 0.25 | 0.25 | 0.4 | 0.4
Pedestrian tunnels | Tradable |  | 0 | 0.15 | 0.15 | 0.2 | 0.3 | [7 empty] | Loading docks | Tradable | 0 | 0.5 | 0.5 | 0.5 | 0.5
Plaza areas | Tradable |  | 0 | 0.14 | 0.14 | 0.16 | 0.2 | [7 empty] | Sales canopy | Tradable | 0 | 0.6 | 0.6 | 0.8 | 1
Primary building entrances | Tradable | [6 empty] | 0 | 20 | 20 | 30 | 30 |  |  | Outdoor sales area | Tradable | 0 | 0.25 | 0.25 | 0.5 | 0.7
Roadway/parking, entry, trailhead, toilet facility | Nontradable | [12 empty] | 0 | Street frontage for vehicle sales | Tradable | [5 empty] | 0 | 0 | 10 | 10 | 30
Sales canopy | Tradable |  | 0 | 0.6 | 0.6 | 0.8 | 1 | [7 empty] | Building façade | Nontradable | 0 | 0 | 0.1 | 0.15 | 0.2 | 0 | 0 | 2.5 | 3.75 | 5
Special feature areas | Tradable |  | 0 | 0.14 | 0.14 | 0.16 | 0.2 | [7 empty] | ATM or Night Depository | Nontradable | [10 empty] | 270 | 90
Stairways | Tradable |  | 0 | 0.75 | 1 | 1 | 1 | [7 empty] | Entrances and gatehouse inspection at guarded facilities (uncovered) | Nontradable | 0 | 0.75 | 0.75 | 0.75 | 0.75
Street frontage for vehicle sales | Tradable | [6 empty] | 0 | 0 | 10 | 10 | 30 |  |  | Loading area for emergency service vehicles (uncovered) | Nontradable | 0 | 0.5 | 0.5 | 0.5 | 0.5
Uncovered parking areas and drive | Tradable |  | 0 | 0.04 | 0.06 | 0.1 | 0.13 | [7 empty] | Drive-thrus | Nontradable | [11 empty] | 400
Walkways >= 10' wide | Tradable |  | 0 | 0.14 | 0.14 | 0.16 | 0.2 | [7 empty] | Parking near 24-hour retail entrances (main only) | Nontradable | [11 empty] | 800
Walkways less than 10' wide | Tradable | [6 empty] | 0 | 0.7 | 0.7 | 0.8 | 1 |  |  | Roadway/parking, entry, trailhead, toilet facility | Nontradable | [11 empty] | 0

## GSG Avg Rotations
INSTRUCTIONS: If the modeling parameters call for averaging 4 rotations, enter the data into each of the white columns. If the modeling protocol does not require averaging the 4 rotations, enter the data into only the column labeled "0'" (do not enter '0' into the columns labeled 90, 180, 270).
4a | Baseline Rotations
GSG Baseline Model
|  | 0' |  | 90' |  | 180' |  | 270' |  | Average of 4 rotations
Annual usage (kwh/therm)
|  | kwh | therm | kwh | therm | kwh | therm | kwh | therm | kwh | therm
Interior Lighting | [9 empty] | 0 | 0
Misc. Equip. | [9 empty] | 0 | 0
Space Heat | [9 empty] | 0 | 0
Space Cool | [9 empty] | 0 | 0
Heat Rejection | [9 empty] | 0 | 0
Pumps & Misc | [9 empty] | 0 | 0
Vent Fans | [9 empty] | 0 | 0
Dom. Hot Water | [9 empty] | 0 | 0
Exterior Lighting | [9 empty] | 0 | 0
Exterior Misc. | [9 empty] | 0 | 0
TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual cost ($)
Electric
Gas
Steam
Other
TOTAL |  | 0 |  | 0 |  | 0 |  | 0 |  | 0

## SCA Exec Summary
School Information
School Name
Address
Building Type |  |  |  | Student population
Number of Stories |  |  |  | Students served by kitchen
Submission
Template Used
Date
Baseline Information
LL32 Baseline |  | ASHRAE 90.1-2013 ECB
GSG Baseline |  | ASHRAE 90.1-2010 PRM
GSG Version |  | 2019 Rating System
% Renovation |  | 0%
Energy Modeling Information
Drawing Set
| Modeling Software & version | 0
| Weather File | 0
Window/Wall Ratio
Total Modeled Square Feet
| Area of plenums/ dummy zones | 0
| Net Modeled Area | 0
| Unconditioned Area |  |  | Kitchen area | 0
| Conditioned SQFT | 0 |  | Kitchen % of building | #DIV/0!
| Proposed Unmet Load Hours | 0
| LL32 Baseline Unmet Load Hours | 0
GSG Baseline Unmet Load Hours
LL32 Results |  |  | GSG Results
| LL32 Regulated Electric Cost |  |  | GSG Baseline Electric Cost
| LL32 Regulated Gas Cost |  |  | GSG Baseline Gas Cost
| LL32 Unregulated Electic Cost | 0 |  | Proposed Electric Cost | 0
| LL32 Unregulated Gas Cost | 0 |  | Proposed Gas Cost | 0
| Proposed Regulated Electric Cost |  |  | GSG Baseline Total Cost | 0
| Proposed Regulated Gas Cost |  |  | Proposed Total Cost
| LL32 Baseline Regulated Cost | 0 |  | Total Cost Savings
| Proposed Regulated Cost | 0 |  | GSG Baseline Site EUI | 0
| Regulated Cost Savings |  |  | Proposed Site EUI | 0
| LL32 Baseline Total Cost |  |  | Site EUI Savings
| Proposed Total Cost |  |  | GSG Source EUI
| Total Cost Savings |  |  | Proposed Source EUI
| LL32 Baseline Site EUI | 0 |  | Source EUI Savings
| Proposed Site EUI | 0
| Site EUI Savings |  |  | GSG Compliant? | Compliant
| LL32 Source EUI |  |  | Optimize Energy Points
Proposed Source EUI
Source EUI Savings
| LL32 Compliant? | Compliant
Utility Rates
| Proposed Carbon (Ton CO2e) |  |  | Average Electricity Cost ($/kWh)
| Proposed Carbon (Ton CO2e/ft2) |  |  | Average Gas Cost ($/Therm)
Note on D21: Should be within 3% of gross building area
Note on D22: Matches LV-B area
Note on D23: Includes area of zones that are required for modeling, but do not contribute to actual floor area, such as plenums
Note on D24: Should be within 1% of gross building area
Note on D25: Includes unconditioned areas, such as shafts, that contribute to floor area
Note on D53: Valid for buildings with electricity and natural gas only

## SCA ECM Summary
Energy Efficiency Measure Summary
Note: Only required for measures that are NOT included in proposed design
Have additional measures been included for evaluation that are not part of the proposed design?
No additional measures modeled. This form does not need to be completed
Measure # |  | Electricity |  | Natural Gas |  | Total Cost | Source Energy Use
| Description of Measure | kWh | Cost | Therms | Cost |  | Total (kBtu) | EUI (kBtu/ft2)
0 | Proposed Design |  | 0 |  | 0 | 0 | #VALUE!
1 | [5 empty] | 0 | 0
2 | [5 empty] | 0 | 0
3 | [5 empty] | 0 | 0
4 | [5 empty] | 0 | 0
5 | [5 empty] | 0 | 0
6 | [5 empty] | 0 | 0
7 | [5 empty] | 0 | 0
8 | [5 empty] | 0 | 0
9 | [5 empty] | 0 | 0
10 | [5 empty] | 0 | 0

## SCA Usage Summary
5 | Energy Modeling Usage Summary
|  | LL32 Baseline ASHRAE 90.1-2013 ECB |  | GSG Baseline ASHRAE 90.1-2010 |  | Proposed Model
|  | Electric Usage (kwh) | Gas/Steam Usage (Therm) | Electric Usage (kwh) | Gas/Steam Usage (Therm) | Electric Usage (kwh) | Gas/Steam Usage (Therm) | Energy Savings Per End Use (%) vs LL32 | Energy Savings Per End Use (%) vs GSG
Interior Lighting |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Misc. Equip. |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Space Heat |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Space Cool |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Heat Rejection |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Pumps & Misc |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Vent Fans |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Dom. Hot Water |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Exterior Lighting |  |  | 0 | 0 | 0 |  | 0 | #VALUE! | 0%
Exterior Misc. |  | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TOTAL |  | 0 | 0 |  | 0 |  | 0 | #VALUE! | 0%
5a | Energy Related Design Features
List energy related features that are included in the design and contribute to the energy savings in Section 5.
Include any ECM's that are not part of the SCA standard design requirements

## SCA Window Summary
6b | Vertical Fenestration
Model Input Parameter |  |  | LL32 Baseline ASHRAE 90.1-2013 ECB |  |  |  | GSG Baseline ASHRAE 90.1-2010 |  |  |  | Proposed Case
|  | Item # | Description (from ASHRAE) | U-factor | SHGC | VLT | Description (from ASHRAE) | U-factor | SHGC | VLT | Description (from design) | U-factor | SHGC | VLT
Vertical |  | 1
Vertical |  | 2
Vertical |  | 3
Vertical |  | 4
Vertical |  | 5
Vertical |  | 6
Vertical |  | 7
Skylight |  | 1
Skylight |  | 2
Shading Devices |  |  | ☐No shading projections, manual shading devices, or self-shading have been modeled. |  |  |  | ☐No shading projections, manual shading devices, or self-shading have been modeled. |  |  |  | List any permanent or auto-controlled shading devices:
|  |  | ☐Any shading by adjacent structures has been modeled identically to the proposed case. |  |  |  | ☐Any shading by adjacent structures has been modeled identically to the proposed case.

## SCA Wall Summary
| Space-Conditioning Category | Item # | LL32 Baseline ASHRAE 90.1-2013 ECB |  | GSG Baseline ASHRAE 90.1-2010 |  | Proposed Case
Model Input Parameter |  |  | Description | U-factor/ C-factor/ F-factor | Description | U-factor/ C-factor/ F-factor | Description | Assembly U-factor/ C-factor/ F-factor | % of above-grade wall
Above-Grade Exterior Wall Construction | Non-Residential | 1 | Mass | U-0.104 | Steel-Framed | U-0.064
2
3
4
5
6
7
8

## SCA Wall Summary (2)
| Space-Conditioning Category | Item # | LL32 Baseline ASHRAE 90.1-2013 ECB |  | GSG Baseline ASHRAE 90.1-2010 |  | Proposed Case
Model Input Parameter |  |  | Description | U-factor/ C-factor/ F-factor | Description | U-factor/ C-factor/ F-factor | Description | Assembly U-factor/ C-factor/ F-factor | % of above-grade wall
Roof Construction | Non-Residential | 1 | Insulation Entirely Above Deck | U-0.032 | Insulation Entirely Above Deck | U-0.048
|  |  | Solar Reflectance | SR = | Solar Reflectance | SR = | Solar Reflectance
2
|  |  | Solar Reflectance | SR = | Solar Reflectance | SR = | Solar Reflectance
Below-Grade Exterior Wall Construction | Non-Residential | 1 | Below-Grade Wall | C-0.119 | Below-Grade Wall | C-1.140
2
Exposed Floor Construction |  | 1
Slab-On-Grade Floors |  | 1
Opaque Doors | Non-Residential | 1 | Swinging | U-0.500
2

## SCA Interior Lighting Summary
Space Type (Table 9.6.1) or Building Area Type (Table 9.5.1) | Total Area Space/Blg Type (ft2) | LL32 Baseline ASHRAE 90.1-2013 ECB |  |  | GSG Baseline ASHRAE 90.1-2010 |  |  | Proposed Case
|  | Auto. Controls (Yes/No) | Daylight Ctrls (Yes/No) | Modeled LPD | Auto. Controls (Yes/No) | Daylight Ctrls (Yes/No) | Modeled LPD | Auto. Controls (Yes/No) | Daylight Ctrls (Yes/No) | Modeled LPD
|  |  |  | (W/ft2) |  |  | (W/ft2) |  |  | (W/ft2)
|  | Yes | Yes |  |  |  |  | Yes | Yes
|  | Yes | Yes |  |  |  |  | Yes | Yes
|  | Yes | Yes |  |  |  |  | Yes | Yes
|  | Yes | No |  |  |  |  | Yes | No
|  | Yes | No |  |  |  |  | No | No
|  | Yes | No |  |  |  |  | No | No
|  | Yes | No |  |  |  |  | Yes | No
|  | Yes | No |  |  |  |  | Yes | No
|  | Yes | Yes |  |  |  |  | Yes | Yes
|  | Yes | No |  |  |  |  | Yes | No
|  | Yes | No |  |  |  |  | Yes | No
|  | No | No |  |  |  |  | No | No
|  | Yes | Yes |  |  |  |  | Yes | Yes
|  | No | No |  |  |  |  | No | No
|  | No | Yes |  |  |  |  | No | Yes
Total

## SCA Ext LPD Process Equ
Exterior Lighting Power
| LL32 Baseline (Watts) | GSG Baseline (Watts) | Proposed Design (Watts)
Tradable Lighting Power
Non-Tradable Lighting Power
Base Site Allowance
Total Lighting Power
Process/Receptacle Equipment
Space Type (or Equipment Type) | Space Area (or # Equip.) | Proposed Design Equipment Power Density (W/SF) | LL32 Baseline Design Equipment Power Density (W/SF) | GSG Baseline Design Equipment Power Density (W/SF)
| SQFT | W/SF | W/SF
TOTAL
Kitchen Equipment
Population Served by Kitchen
Kitchen Type |  | Full Kitchen
Cooking Fuel |  | Electric | Expected Value
Total Kitchen Plug Load
Kitchen Plug Load Schedule
Total Kitchen Source Load
Source Load Schedule |  | Select Fuel Type

## SCA Service HW
Service Hot Water Systems
Model Input Parameter | LL32 Baseline ASHRAE 90.1-2013 ECB |  | GSG Baseline ASHRAE 90.1-2010 |  | Proposed Case
| Description | Units | Description | Units | Description | Units
System Type & Fuel | 0 |  | 0 |  | 0
Input Rating | 0 | kBtu/h |  | kBtu/h | 0 | kBtu/h
Efficiency | 0 | EF |  | Et | 0 | Et
Storage Volume | 0 | Gal |  | Gal | 0 | Gal
Storage Temperature | 0 | °F |  | °F | 0 | °F
Peak HW Demand | 0 | GPM |  | GPM | 0 | GPM
Number of Primary DHW pumps | 0 | # |  | # | 0 | #
Primary DHW Pump Power | 0 | kW |  | kW | 0 | kW
Primary DHW Pump Control | 0 |  |  |  | 0

## SCA HVAC Air Class
Air-Side HVAC Systems
| HVAC System / Group LL32 Baseline ASHRAE 90.1-2013 ECB |  | HVAC System / Group GSG Baseline ASHRAE 90.1-2010 |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Description | Units
System Type
System Designation(s)
# of Similar Systems
Total Cooling Capacity |  | kBtu/h |  | kBtu/h |  | kBtu/h
*Table 6.8.1 Unitary Cooling Capacity Range |  | kBtu/h |  | kBtu/h |  | kBtu/h
*Unitary Cooling Eff. (EER or SEER) |  | EER |  | EER |  | EER
*Unitary Cooling Part-load Eff. (if applicable) |  | IEER |  | IEER |  | IEER
Total Heating Capacity |  | kBtu/h |  | kBtu/h |  | kBtu/h
*Table 6.8.1 Unitary Heating Capacity Range |  | kBtu/h |  | kBtu/h |  | kBtu/h
*Unitary Heating Efficiency |  | COP |  | COP |  | COP
*Fan Control
Supply Airflow |  | cfm |  | cfm |  | cfm
Outdoor Airflow |  | cfm |  | cfm |  | cfm
*Demand Control Ventilation
*Economizer High-Limit Shutoff (°F)
Exhaust Air Energy Recovery Systems
*Exhaust Air Energy Recovery Effectiveness
Supply Fan Power |  | kW |  | kW |  | kW
Return/Relief Fan Power |  | kW |  | kW |  | kW
Exhaust Fan Power |  | kW |  | kW |  | kW
System Fan Power |  | kW |  | kW |  | kW
Allowed Fan Power: |  | kW |  | kW |  | kW
Pressure Drop Adjustments | cfm | in w.c. | cfm | in w.c.
Fully Ducted Return |  | 0.5 |  | 0.5
Filters: MERV 13-15 |  | 0.9 |  | 0.9
Heat Recovery Device |  | 0.6 |  | 0.6 | Based on 50% efficiency for 1 stream. Enter cfm for supply + exhaust through ERV
Sound Attenuation Section |  | 0.15 |  | 0.15
Other
Other
Equipment Included (per Mechanical Schedules)

## SCA HW Summary
Hot Water or Steam
Model Input Parameter | LL32 Baseline ASHRAE 90.1-2013 ECB |  | GSG Baseline ASHRAE 90.1-2010 |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Description | Units
Number and Type of Boilers | Gas Fired, Hot Water |  |  |  | Modulating Condensing w/ 30% propylene glycol solution in primary loop
Total Boiler Capacity |  | kBTU |  |  |  | kBTU
Boiler Efficiency |  |  |  |  | 93% (@RWT=120°F) 86% (@RWT=140°F) | %
Hot Water or Steam (HHW) Supply Temp | SWT=180°F @ OAT≤20°F SWT=150 °F @ OAT≥50°F | °F |  | °F | RWT=140°F @ OAT≤20°F RWT=120 °F @ OAT≥50°F | °F
HHW ΔT | 50 | °F |  | °F | 40 | °F
HHW Temp Reset Parameters | Outdoor air – supply water temp reset |  |  |  | Outdoor air – return water temp reset
HHW Loop Configuration |  |  |  |  | Primary Only
Number of Primary HHW Pumps |  |  |  | # |  | #
Primary HHW Pump Power |  |  |  |  | 19 | W/GPM
Primary HHW Pump Flow |  | gpm |  | gpm |  | gpm
Primary HHW Pump Control
Number of Secondary HHW Pumps |  | # |  | # |  | #
Secondary HHW Pump Power
Secondary HHW Pump Flow |  | gpm |  | gpm |  | gpm
Secondary HHW Pump Control
Other (describe)
Other (describe)
Other (describe)
Other (describe)

## SCA CHW Summary
Chilled Water
Model Input Parameter | GSG Baseline ASHRAE 90.1-2010 |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units
# and Type of Chillers (and capacity of chiller if more than 1 type or size) | 0- Building area < 150,000 |  | Air cooled w/ 30% propylene glycol solution in primary loop
Total Chiller Capacity |  |  | 0 | 0
Chiller Efficiency - Full Load |  |  | 1.297 | kW/ton
Chiller Efficiency - Part Load |  |  | 0.884 | kW/ton
Chilled Water (CHW) Supply Temp |  | °F | 44 | °F
CHW ΔT |  | °F | 12 | °F
CHW Supply Temp Reset Parameters |  |  | Demand Reset
CHW Loop Configuration |  |  | 0
Number of Primary CHW Pumps |  | # | 0 | #
Primary CHW Pump Power |  |  | 0 | 0
Primary CHW Pump Flow |  | gpm | 0 | gpm
Primary CHW Pump Control |  |  | 0
Number of Secondary CHW Pumps |  | # | 0 | #
Secondary CHW Pump Power |  |  | 0 | 0
Secondary CHW Pump Flow |  | gpm | 0 | gpm
Secondary CHW Pump Control |  |  | 0
Water-Side Economizer
Water-Side Energy Recovery
Number of Cooling Towers/Fluid Coolers
Cooling Tower Fan Power
Cooling Tower Fan Control
Condenser Water (CW) Leaving Temp |  | °F
CW ΔT |  | °F
CW Loop Temp Reset Parameters
Number of CW Pumps |  | #
CW Pump Power
CW Pump Flow |  | gpm
CW Pump Control
Other (describe)
Other (describe)
Other (describe)
Other (describe)

## General Checklist
eQuest Model Review Checklist
Yes/No | General information | Response
| Does the project area include a kitchen? | N/A
| Verify the kitchen type (full gas, full electric, or warming) been modeled per the proposed design and the kitchen loads reflect the number of students in the POR. | N/A
| Verify the occupancy and ventilation requirements in the classrooms been updated to match the POR. | N/A
| Is the net modeled project area within 1% of the design area? | No
N/A | Describe any changes between this submission and the previous submission:
N/A
N/A | Describe deviations from the SCA Standard Details (Including SCA approved ECMs)
N/A
Describe deviations in the floor area that result in a net modeled project area that exceeds the design area by more than 1%.
Yes/No | Automatic Checks | Explanation, if required
Yes | The "Ext Usage" EFLH is more than 4,500 per the report design value. Exterior lighting is only to be run during dark hours, even worst cases should not exceed this value. Please correct or provide an explanation. |  | 0
Yes | The sum of the hours above cooling throttling range and heating throttling is above 300. Please correct.
Yes | The total amount of hours the design is out of range (heating + cooling) differs from the GSG baseline by more than 50 hours. Please correct or provide an explanation. |  | 0
No | The calculated lighting EFLH is -1 hrs. Between 1,600 and 2,500 is expected using the template schedules. Please correct or provide explanation. |  | -1
No | The Misc Equipment is -100.0% of the total electricity. It is expected to be between 20-35%. Please correct or provide an explanation. |  | -100%
Yes | The Misc Equipment is not the same in baseline and proposed designs. Please correct or provide an explanation.
No | The Domestic Hot Water is -100.0% of the total heating fuel. It is expected to be less than 10% for projects without kitchens and 10-20% for projects with kitchens. Please correct or provide an explanation. |  | -1 | 0
No | The proposed Space Cooling is -100.0% of the total electricity. It is typically less than 30%. Please correct or provide an explanation |  | -1
No | The proposed Vent Fans is -100.0% of the total electricity. It is typically less than 30%. Please correct or provide an explanation. |  | -1
Yes | The GSG baseline does not show Zero electric use for heating. Electric heating should only happen under special circumstances. Please correct or provide an explanation.

## Output Checklist
eQuest Model Review Checklist- Output Report Verification
BEPU report information | Yes/No | Explanation, if required | Reference Number
Is the "Weather file" consistent with the building location. | No |  | 1
Is "Task Lighting" the same between baselines and proposed cases? If no, fix or provide supporting documentation. | No |  | 3
Is the split between electricity and natural gas "Space Heating" consistent with the design and report documentation? | No |  | 6
Is the "Pumps and Aux" EFLH consistent with the design? i.e. total pump EFLH should be roughly equal to the sum of respective plant EFLH for plants with pumps. | No |  | 9
Is the split between electricity and natural gas "Domest Hot Wtr" consistent with the DHW system design? | No |  | 11
Is “Percent of hours any plant load not satisfied” 0%? If no, fix or provide supporting documentation. | No |  | 14
Is "Heat Rejection" zero ? If no, provide an explanation. Heat rejection should only be more than zero for water-cooled units (GSG Baseline > 150,000 ft2 and designs that deviate from the standard) | No |  | 14
ES-D report information | Yes/No | Explanation, if required | Reference Number
Do the utility costs match the values in the report? | No |  | 1
LV-B report information | Yes/No | Explanation, if required | Reference Number
Are the lighting power densities consistent with the report/photometric drawing/code requirements? Have lighting schedules been assigned that reflect mandatory controls (template defaults should be sufficient)? | No |  | 1
Are the equipment power densities consistent with the input summary? | No |  | 2
LV-D report information | Yes/No | Explanation, if required | Reference Number
Is the "Window Area" divided by the "Window+Wall Area" for the "All Walls" line consistent with the report window to wall ratio? | No |  | 1
Is the roof area consistent with the footprint of the building? | No |  | 2
Select a few representative wall definitions, are their U-values consistent with report values? Note: The LV-D and LV-I reports calculations are not consistent with the protocol established by ASHRAE 90.1 Appendix A. The interior air film coefficient default does not account for the orientation of the construction. The LV-I U-value calculation does not consider the exterior air film, and the LV-D U-value calculation uses a different value than specified by ASHRAE 90.1 Appendix A. During the simulation, eQuest calculates the exterior air film hourly based on the wind speed from the weather file. | No |  | 3
Select a few representative window definitions, are their U-values consistent with report values? Note: The window U-values include an exterior film with R-value = 0.3. NFRC uses 0.17 to calculate the U-factor. The U-value from the LV-D report will be 3-5% lower than reported value. | No |  | 4
Is the total envelope area (façade and roofs) within 1% of the architectural area take-offs? If NO, please provide an explanation of the deviations. | No |  | 5
LV-H report information | Yes/No | Explanation, if required | Reference Number
Is the weighted average U-value consistent with the report values for frame and glass U-values? | No |  | 1
Is the "Glass Shading Coeff" and "Glass Visible Trans" consistent with the report and design values? | No |  | 2
Is a "setback" modeled? If yes, is it consistent with the design? No setback should be modeled in the baseline condition for new construction projects. | No |  | 3
LV-I report information | Yes/No | Explanation, if required | Reference Number
Are U-Values within the acceptable range of the reported values? Note: Compare U-values reported in the LV-D report to those in the LV-I report. The LV-I report values will be higher, with variation depending on the thermal properties of the wall. LV-I values may vary from LV-D report as follows LV-D U-value - LV-I Deviation <0.07 - <5% higher 0.07 - 0.13 - 5-10% higher 0.13 - 0.17 - 10-15% higher 0.17 - 0.20 - 15-20% higher | No |  | 1
Are "Delayed" surface types used for exterior wall and roof construction definitions? If no, explain where building massing is being accounted for in the model. | No |  | 2
Are the "Number of Response Factors" consistent with report mass vs. framed construction? | No |  | 3
SV-A report information | Yes/No | Explanation, if required | Reference Number
Has an SV-A report been provided for all systems referenced in the report? | No |  | NA
Is there 1-1 correspondence in the number of systems between the LL32 baseline and proposed design? | No |  | NA
Is there one system per floor for the GSG baseline, with the exception of the public assembly spaces and 24hr data rooms? | No |  | NA
Are "Capacity (CFM)" and "Power Demand" consistent with the report? | No |  | 1
Is the "Outside Air Ratio" consistent with the ratio calculated using the report values? | No |  | 2
Is the "Outside Air Ratio" lower than the "Minimum Flow"? If no, correct this. Note: eQuest has a known bug where the software will not reset minimum flow up to the outside air ratio. | No |  | 3
Are there "Baseboards" defined in the Proposed system? Is this consistent with the report? No baseboards should be defined in the baseline systems. | No |  | 4
The deviation of modeled equipment sizes relative to the mechanical systems is greater than 1% for general systems and greater than 5% for motors smaller than 1HP, air flows less than 100 CFM and coil sizes less than 12 kBtu/h. If yes, provide an explanation. | No |  | 5
PV-A report information | Yes/No | Explanation, if required | Reference Number
Is the "rated capacity" of proposed equiment consistent with the report and design values? | No |  | 1
Does pump "Head" match between proposed and LL32 baseline? | No |  | 2
Calculate the GSG baseline "Power"/"Flow" for secondary and primary pumps. Does this value add up to 19 W/gpm for heating, 22 W/gpm for cooling, and 19 W/gpm for the condenser loop? Chilled and condenser water loops should be present in schools >150,000 ft2 only. | No |  | 3
Are "Capacity Control" values consistent with the report? Note: If a loop is served by more than 1 pump, the variable speed pumps will be reported as "VFD & STAGED" | No |  | 4
The deviation of modeled equipment sizes relative to the mechanical systems is greater than 1% for general equipment and greater than 5% for motors smaller than 1 HP or water flows less than 100 GPM. If yes, provide an explanation. | No |  | 5
PS-E report information | Yes/No | Explanation, if required | Reference Number
Do "Task Lighting", "Misc Equip", "Domest Hot Wtr", and "Ext Usage" all have the same Max kW for all months? If not, is this explained? | No |  | 2
If daylighting is specified, does "lights" Max kW have a minimum in the summer and maximum in the winter? Note: if daylighting is claimed but not modeled the lighting use will only be determined by the schedule and the peak will not vary. The peak vaires becaue of the change in solar angle from summer to winter. The use varies also because the number of hours of daylight changes as well. When daylighting is modeled, the EFLH will not match the schedule. | No |  | 3
Is "Space Heating" zero for June to Sept? If not, is it explained in the report? Is there reheat specified? | No |  | 4
Is "space cooling" minimal in the winter? Are these values consistent with the data room equipment sizes? Note: peaks in winter should be equal to the power input of data or EMR dedicated units. | No |  | 5

## GSG_List (hidden)
Non-Residential | [6 empty] | 40 | Yes | kW | # | kW
Residential | [7 empty] | No | kBtu/h | SQFT | W/SF
Semiheated
| Non-Residential | Residential | Semiheated |  |  |  |  | Section 11 ECB | EF | kBTU/h | EER | Et
Nonmetal framing (all) | U-0.40 |  | U-0.51 |  |  |  |  | Appendix G PRM | SL | tons | SEER | Ec
Metal framing (Curtainwall/Storefront) | U-0.50 |  | U-0.73 | [5 empty] | Et | kW |  | AFUE
Metal framing (all other) | U-0.55 |  | U-0.81 | [5 empty] | COP | Btuh |  | COP
Metal framing (entrance door) | U-0.85 |  | U-0.77 | [8 empty] | HSPF
| Non-Residential | Residential | Semiheated
Nonmetal framing (all) | 0.4 | 0.4 | NR
Metal framing (Curtainwall/Storefront) | 0.4 | 0.4 | NR
Metal framing (all other) | 0.4 | 0.4 | NR
Metal framing (entrance door) | 0.4 | 0.4 | NR
Skylights | Non-Residential | Residential | Semiheated
0% - 2.0% | U-0.69 | U-0.50 | U-1.15
2.1%+ | U-0.69 | U-0.50 | U-1.15
Skylights | Non-Residential | Residential | Semiheated
0% - 2.0% | 0.49 | 0.4 | NR
2.1%+ | 0.39 | 0.4 | NR
| Non-Residential | Residential | Semiheated
Insulation Entirely Above Deck | U-0.048 | U-0.032 | U-0.093
| Non-Residential | Residential | Semiheated
Steel-Framed | U-0.064 | U-0.064 | U-0.124
| Non-Residential | Residential | Semiheated
Below-Grade Wall | C-1.140 |  | C-1.140
| Non-Residential | Residential | Semiheated
Mass | U-0.087 | U-0.051 | U-0.107
Steel-Joist | U-0.038 | U-0.038 | U-0.052
Wood-Framed and Other | U-0.033 | U-0.033 | U-0.051
| Non-Residential | Residential | Semiheated
Unheated | F-0.730 | F-0.520 | F-0.7300
Heated | F-0.860 | F-0.688 | F-0.900
| Non-Residential | Residential | Semiheated
Swinging | U-0.7 | U-0.500 | U-0.700
Nonswinging | U-1.500 | U-0.500 | U-1.450
System 5: Packaged VAV with Reheat | VAV
System 7: VAV with reheat | VAV
System 3: PSZ-AC | Constant Volume
System 9: Heating and Ventilation | Constant Volume
System 6: Packaged VAV with PFP Boxes | VAV
System 8: VAV with PFP Boxes | VAV
System 4: PSZ-HP | Constant Volume
System 10: Heating and Ventilation (elec) | Constant Volume
LL32 Baseline
ASHRAE 90.1-2013 ECB
ASHRAE 90.1-2016 ECB
GSG Baseline
ASHRAE 90.1-2010 PRM
GSG Version
2009 Rating System
2016 Rating System
2019 Rating System
Source EUI | Factor
Electricity | 2.55
Natural Gas | 1.05
2009 Rating System
New construction % | Renovation % | Weighted | LEED Points
0.05 | 0.03 | 0.05 | 3
0.06 | 0.04 | 0.06 | 4
0.08 | 0.06 | 0.08 | 5
0.1 | 0.08 | 0.1 | 6
0.12 | 0.1 | 0.12 | 7
0.14 | 0.12 | 0.14 | 8
0.16 | 0.14 | 0.16 | 9
0.18 | 0.16 | 0.18 | 10
0.2 | 0.18 | 0.2 | 11
0.22 | 0.2 | 0.22 | 12
0.24 | 0.22 | 0.24 | 13
0.26 | 0.24 | 0.26 | 14
0.28 | 0.26 | 0.28 | 15
0.3 | 0.28 | 0.3 | 16
0.32 | 0.3 | 0.32 | 17
0.34 | 0.32 | 0.34 | 18
0.36 | 0.34 | 0.36 | 19
2016 Rating System
New construction % | Renovation % | Weighted | LEED Points
-100 | -100 | -100 | Not Compliant
0.05 | 0.03 | 0.05 | 0
0.06 | 0.04 | 0.06 | 1
0.08 | 0.06 | 0.08 | 2
0.1 | 0.08 | 0.1 | 3
0.12 | 0.1 | 0.12 | 4
0.14 | 0.12 | 0.14 | 5
0.16 | 0.14 | 0.16 | 6
0.18 | 0.16 | 0.18 | 7
0.2 | 0.18 | 0.2 | 8
0.22 | 0.2 | 0.22 | 9
0.24 | 0.22 | 0.24 | 10
0.26 | 0.24 | 0.26 | 11
0.29 | 0.27 | 0.29 | 12
0.32 | 0.3 | 0.32 | 13
0.35 | 0.33 | 0.35 | 14
0.38 | 0.36 | 0.38 | 15
0.42 | 0.4 | 0.42 | 16
0.46 | 0.44 | 0.46 | 17
0.5 | 0.48 | 0.5 | 18
GSG Baseline Chiller
0- Building area < 150,000
1
2
Kitchen Equipmnt
Kitchen Type
Full Kitchen
Warming Kitchen
Cooking Fuel
Gas
Electric
N/A
Kitchen Plug Load Schedule | Full Kitchen
401-KIT-EQP-YR | 401-KIT-EQP-YR | 101-WKIT-EQP-YR
501-KIT-EQP-YR | 501-KIT-EQP-YR | 301-WKIT-EQP-YR
701-KIT-EQP-YR | 701-KIT-EQP-YR
901-KIT-EQP-YR | 901-KIT-EQP-YR
1K-KIT-EQP-YR | 1K-KIT-EQP-YR
Source Load Schedule | Electric | Full Kitchen
401-KIT-SRC-E-YR | 401-KIT-SRC-G-YR | 401-KIT-SRC-E-YR
501-KIT-SRC-E-YR | 501-KIT-SRC-G-YR | 501-KIT-SRC-E-YR
1K-KIT-SRC-E-YR | 1K-KIT-SRC-G-YR | 1K-KIT-SRC-E-YR
Kitchen Check
Population | Equipment kW | Equipment Sch | Gas Source | Electric Source | Gas Source Sch | Elec Source Sch
0
1 | 35.7 | 101-WKIT-EQP-YR
301 | 40.9 | 301-WKIT-EQP-YR
401 | 31.1 | 401-KIT-EQP-YR | 310000 | 249200 | 401-KIT-SRC-G-YR | 401-KIT-SRC-E-YR
501 | 46.6 | 501-KIT-EQP-YR | 408000 | 287300 | 501-KIT-SRC-G-YR | 501-KIT-SRC-E-YR
701 | 50.8 | 701-KIT-EQP-YR | 408000 | 287300 | 501-KIT-SRC-G-YR | 501-KIT-SRC-E-YR
901 | 54.6 | 901-KIT-EQP-YR | 408000 | 287300 | 501-KIT-SRC-G-YR | 501-KIT-SRC-E-YR
1000 | 65 | 1K-KIT-EQP-YR | 506000 | 325400 | 1K-KIT-SRC-G-YR | 1K-KIT-SRC-E-YR

## Instructions
WORKBOOK COLOR LEGEND
Do not edit: information
Do not edit: formulas
Do not edit: error
User edit: drop-down menu
User edit: fill in box

## 1,2,3 Information
Enter information for sections 1, 2 and 3 - incorporate in the drawing set.
Must be typewritten
1 | Location Information
| House No(s) | Street Name
| Borough | Block | Lot | BIN |  | CB No.
| Work on Floor(s) |  |  |  | Apt/Condos No(s)
2 | Applicant Information
| Last Name |  | First Name |  |  |  |  | Middle Initial
| Business Name |  |  |  | Business Telephone
| Business Address |  |  |  | Business Fax
| City | State |  | Zip |  |  | Mobile Telephone
| Email |  |  |  |  | License Number
3 | Energy Modeling Information
Modeling Software & version
Weather File
Modeled Square Feet
Conditioned SQFT
Proposed Unmet Load Hours
Baseline Unmet Load Hours
Proposed Site EUI (kBtu/sf)
Baseline Site EUI (kBTU/SF)

## 4. Purchased Energy Rates
3 | Energy Modeling Protocol (select)
Section 11 ECB
4 | Purchased Energy Rates
Fuel |  | Utility Rate Provider/Rate Structure (i.e ConEd) | Virtual Utility Rate ($/unit) | Baseline Design Total Charge ($) | Virtual Utility Rate ($/unit) | Proposed Design Total Charge ($) | Supporting Doc. Location | Model Output Report
Electric |  | DES Electric | [5 empty] | ES-D
Gas |  | DES Gas | [5 empty] | ES-D
Steam
Other: | [6 empty] | COST SAVINGS | COMPLIES?
TOTAL
4A | Performance Cost Index - Appendix G ONLY
|  | Baseline Building | Proposed Building
Building Performance Factor |  | 0.49 | School
Baseline Regulated Cost
Baseline Unregulated Cost |  | 0 | 0
Total Energy Cost
Performance Cost Index
Note on E7: Department of Buildings: Input data on sheet 4a to populate baseline data

## 4a. Avg. Rotations (hidden)
INSTRUCTIONS: If the modeling parameters call for averaging 4 rotations, enter the data into each of the white columns. If the modeling protocol does not require averaging the 4 rotations, enter the data into only the column labeled "0'" (do not enter '0' into the columns labeled 90, 180, 270).
4a | Baseline Rotations
Baseline Model
|  | 0' |  | 90' |  | 180' |  | 270' |  | Average of 4 rotations |  | Model Output Location (Report)
Annual usage (kwh/therm)
|  | kwh | therm | kwh | therm | kwh | therm | kwh | therm | kwh | therm
Interior Lighting |  | 2000 | [7 empty] | 2000 | 0 | BEPU
Misc. Equip. |  |  | 60 | [6 empty] | 0 | 60 | BEPU
Space Heat | [9 empty] | 0 | 0 | BEPU
Space Cool | [9 empty] | 0 | 0 | BEPU
Heat Rejection | [9 empty] | 0 | 0 | BEPU
Pumps & Misc | [9 empty] | 0 | 0 | BEPU
Vent Fans | [9 empty] | 0 | 0 | BEPU
Dom. Hot Water | [9 empty] | 0 | 0 | BEPU
Exterior Lighting | [9 empty] | 0 | 0 | BEPU
Exterior Misc. | [9 empty] | 0 | 0 | BEPU
TOTAL |  | 2000 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 60 | BEPU
Annual cost ($)
Electric |  | 18000 | [7 empty] | 18000 |  | ES-D
Gas |  | 1000 | [7 empty] | 1000 |  | ES-D
Steam | [11 empty] | ES-D
Other | [11 empty] | ES-D
TOTAL |  | 19000 |  | 0 |  | 0 |  | 0 |  | 19000

## 5. Usage Summary
5 | Energy Modeling Usage Summary
|  | Baseline Model |  |  | Proposed Model
|  | Electric Usage (kwh) | Gas/Steam Usage (Therm) | Other Usage (i.e. chilled water) (indicate units) | Electric Usage (kwh) | Gas/Steam Usage (Therm) | Other Usage (i.e. chilled water) (indicate units) | Energy Savings Per End Use (%) | Cost Savings per End Use (%) | Model Output Location (Report)
Interior Lighting | [9 empty] | BEPU
Misc. Equip. | [9 empty] | BEPU
Space Heat | [9 empty] | BEPU
Space Cool | [9 empty] | BEPU
Heat Rejection | [9 empty] | BEPU
Pumps & Misc | [9 empty] | BEPU
Vent Fans | [9 empty] | BEPU
Dom. Hot Water | [9 empty] | BEPU
Exterior Lighting | [9 empty] | BEPU
Exterior Misc. | [9 empty] | BEPU
TOTAL
[6 empty] | #VALUE! |  |  | #VALUE!
5a | Energy Related Design Features
List energy related features that are included in the design and contribute to the energy savings in Section 5.
Reduced lighting power density
Condensing boilers operate at minimum 89% average efficiency
Air-cooled chiller with superior part load

## 6a. Ext. Wall Areas
6a | Above-Grade Wall & Fenestration Areas
|  |  | Baseline Case |  |  | Proposed Case |  |  | Supporting Doc. Location | Model Output Report
Multifamily
Above-Grade Wall & Vertical Glazing Area by Orientation |  | Orientation | Window + Wall Area (ft2) | Vertical Glazing Area |  | Window + Wall Area (ft2) | Vertical Glazing Area
|  |  |  | (ft2) | (%) |  | (ft2) | (%)
|  | North | [7 empty] | LV-D
|  | East | [7 empty] | LV-D
|  | South | [7 empty] | LV-D
|  | West | [7 empty] | LV-D
|  | Total | [7 empty] | LV-D
Roof & Skylight Area |  | Roof + Skylight Area (ft2) |  | Skylight Area |  | Roof + Skylight Area (ft2) | Skylight Area |  | Supporting Doc. Location | Model Output Report
|  |  |  | (ft2) | (%) |  | (ft2) | (%)
|  | Total | [7 empty] | LV-D

## 6b. Fenestration
6b | Vertical Fenestration
Model Input Parameter |  | Category (Res/Non-Res) |  | Baseline Case |  |  |  | Proposed Case |  |  |  | Supporting Doc. Location | Model Output Report
|  |  | Item # | Description (from ASHRAE) | U-factor | SHGC | VLT | Description (from design) | U-factor | SHGC | VLT
Vertical |  |  | 1 | [9 empty] | LV-D, LV-H
Vertical |  |  | 2 | [9 empty] | LV-D, LV-H
Vertical |  |  | 3
Vertical |  |  | 4
Vertical |  |  | 5
Vertical |  |  | 6
Vertical |  |  | 7
Skylight |  |  | 1 | [9 empty] | LV-D, LV-H
Skylight |  |  | 2
Shading Devices |  |  |  | ☐No shading projections, manual shading devices, or self-shading have been modeled. |  |  |  | List any permanent or auto-controlled shading devices:
☐Any shading by adjacent structures has been modeled identically to the proposed case.
How were the Proposed case framed assembly fenestration U-factors determined? (Choose one)
☐NFRC testing for site-assembled fenestration
☐NFRC testing for manufactured fenestration assemblies
☐Table A8.2 (windows) and Table A8.1 (skylights)
☐LBNL Window 5 or Window 6 calculations
☐Energy simulation includes separate frame and glazing
☐Other (Describe)_________________________
How were the Proposed case framed assembly fenestration U-factors determined? (Choose one)
☐NFRC testing for site-assembled fenestration
☐NFRC testing for manufactured fenestration assemblies
☐Table A8.2 (windows) and Table A8.1 (skylights)
☐LBNL Window 5 or Window 6 calculations
☐Energy simulation includes separate frame and glazing
☐Other (Describe)_________________________

## 6c. Wall Types
6c | Space-Conditioning Category | Item # | Baseline Case |  | Proposed Case |  |  | Supporting Doc Location | Model Output Report
Model Input Parameter |  |  | Description | U-factor/ C-factor/ F-factor | Description | Assembly U-factor/ C-factor/ F-factor | % of above-grade wall
Roof Construction | Non-Residential | 1 | Insulation Entirely Above Deck | U-0.032 |  |  |  |  | LV-D
|  |  | Solar Reflectance | SR =
2
|  |  | Solar Reflectance | SR =
Above-Grade Exterior Wall Construction | Non-Residential | 1 | Mass | U-0.104 |  |  |  |  | LV-D
2
3
4
5
6
7
8
Below-Grade Exterior Wall Construction | Non-Residential | 1 | Below-Grade Wall | C-0.119 |  |  |  |  | LV-D
2
Exposed Floor Construction |  | 1
Slab-On-Grade Floors |  | 1
Opaque Doors | Non-Residential | 1 | Swinging | U-0.500 |  |  |  |  | LV-I
2

## 6d. Interior LPD-Space Method
Space Type (Table 9.6.1) or Building Area Type (Table 9.5.1) | Total Area Space/Blg Type (ft2) | Baseline Case |  |  | Proposed Case
|  | Auto. Controls (Yes/No) | Daylight Ctrls (Yes/No) | Modeled LPD | Auto. Controls (Yes/No) | Daylight Ctrls (Yes/No) | Modeled LPD | Supporting Doc. Location | Model Output Report
|  |  |  | (W/ft2) |  |  | (W/ft2)
|  | Yes | Yes |  | Yes | Yes |  |  | LV-B
|  | Yes | Yes |  | Yes | Yes
|  | Yes | Yes |  | Yes | Yes
|  | Yes | No |  | Yes | No
|  | Yes | No |  | No | No
|  | Yes | No |  | No | No
|  | Yes | No |  | Yes | No
|  | Yes | No |  | Yes | No
|  | Yes | Yes |  | Yes | Yes
|  | Yes | No |  | Yes | No
|  | Yes | No |  | Yes | No
|  | No | No |  | No | No
|  | Yes | Yes |  | Yes | Yes
|  | No | No |  | No | No
|  | No | Yes |  | No | Yes
Total

## 6d. Interior LPD-Bldg Method
Space Type (Table 9.6.1) or Building Area Type (Table 9.5.1) | Total Area Space/Blg Type (ft2) | Baseline Case |  |  | Proposed Case
|  | Auto. Controls (Yes/No) | Daylight Ctrls (Yes/No) | Modeled LPD | Auto. Controls (Yes/No) | Daylight Ctrls (Yes/No) | Modeled LPD | Supporting Doc. Location | Model Output Report
|  |  |  | (W/ft2) |  |  | (W/ft2)
School/university
Total

## 6e. Ext LPD 6f. Process Equip.
6e | Exterior Lighting Power
|  | Baseline Design (Watts) | Proposed Design (Watts) | Supporting Doc. Location | Model Output Report
Tradable Lighting Power |  |  |  |  | PS-E
Non-Tradable Lighting Power |  |  |  |  | PS-E
Base Site Allowance
Total Lighting Power |  |  |  |  | PS-E
* Use the tab labeled "Ext. LPD Calculator" to automatically fill in the table above
f | Process/Receptacle Equipment
Space Type (or Equipment Type) |  | Space Area (or # Equip.) | Equipment Power Density (W/SF) or (Equip Demand) | Modeling Parameters/ Schedule | Baseline Modeled Identically? (Yes/No) | Supporting Doc. Location | Model Output Report
|  | SQFT | W/SF
TOTAL

## Ext LPD Calculator
Lighting Zone
| 2 | R districts, R districts with C overlays and MX districts
| 600 | Base Site Allowance (watts)
| Area Type | Area Parameters |  |  |  | Length or Area (FT or SQFT) | Proposed Watts | Baseline Watts | Unit Allowances
Tradable Surfaces | Uncovered Parking Areas | Total area of uncovered parking and drive areas (sq.ft): | [6 empty] | 0.06 | W/SF
| Building Grounds | Length of walkways less than 10' wide | [6 empty] | 0.7 | W/SF
|  | Area of walkways greater than 10' wide | [6 empty] | 0.14 | W/SF
|  | Plaza areas (sqft) | [6 empty] | 0.14 | W/SF
|  | Special feature areas (sqft) | [6 empty] | 0.14 | W/SF
|  | Area of stairways (sqft) | [6 empty] | 1 | W/SF
|  | Area of pedestrian tunnels (sqft) | [6 empty] | 0.15 | W/SF
|  | Area of landscaping (sq.ft): | [6 empty] | 0.05 | W/SF
| Building Entrances & Exits | Total door width of primary entrances (ft): | [6 empty] | 20 | W/FT
|  | Total door width of other entrances & exits (ft): | [6 empty] | 20 | W/FT
|  | Area of canopies at entrances or exits (sq.ft): | [6 empty] | 0.25 | W/SF
|  | Loading Docks (sq.ft): | [6 empty] | 0.5 | W/SF
| Sales canopies | Area of canopies over sales functions (sq.ft): | [6 empty] | 0.6 | W/SF
| Outdoor sales areas | Area of sales functions (sq.ft): | [6 empty] | 0.25 | W/SF
|  | Total length of street frontage for vehicle sales (ft): | [6 empty] | 10 | W/FT
Non Tradable Surfaces | Building façades | Area of façade #1 (sqft) |  | Length of façade #1 (ft) |  |  |  |  | 2.5 | W/FT | 5 | 0.1 | 2.5 | 0 | 0
|  | Area of façade #2 (sqft) |  | Length of façade #2 (ft) |  |  |  |  | 2.5 | W/FT |  | 0.1 | 2.5 | 0 | 0
|  | Area of façade #3 (sqft) |  | Length of façade #3 (ft) |  |  |  |  | 2.5 | W/FT |  | 0.1 | 2.5 | 0 | 0
|  | Area of façade #4 (sqft) |  | Length of façade #4 (ft) |  |  |  |  | 2.5 | W/FT |  | 0.1 | 2.5 | 0 | 0
| ATMs |  | # of Locations: |  | Total # of ATMs: |  |  |  | Allowance = 270W per location plus 90W per additional ATM per location.
| Guarded facility entrances | Area of uncovered entrances and gatehouse inspection areas at guarded facilities (sq.ft): | [6 empty] | 0.75 | W/FT
| Emergency Vehicle Loading Area | Area of uncovered loading areas for emergency service vehicles (sq.ft): | [6 empty] | 0.5 | W/FT
| Drive-throughs | # of drive-throughs: | [6 empty] | 400 | Watts/drive thru
| Parking near 24-hour retail entrances (main only) | # of main entrances: | [6 empty] | 800 | Watts/entrance

## 6g. Service HW
6g | Service Hot Water Systems
Model Input Parameter |  | Baseline Design | Units | Proposed Design | Units | Supporting Doc Location | Model Output Report
Multifamily
System Type & Fuel | [6 empty] | PV-A
Input Rating |  |  | kBtu/h |  | kBtu/h |  | PV-A
Efficiency |  |  | EF |  | Et |  | PV-A
Storage Volume |  |  | Gal |  | Gal |  | PV-A
Storage Temperature |  |  | °F |  | °F |  | PV-A
Peak HW Demand |  |  | GPM |  | GPM |  | PV-A
Number of Primary DHW pumps |  |  | # |  | # |  | PV-A
Primary DHW Pump Power |  |  | kW |  | kW |  | PV-A
Primary DHW Pump Control | [6 empty] | PV-A

## 6i. HVAC Air-Side
Air-Side HVAC Systems
| HVAC System / Group (BASELINE DESIGN) |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Supporting Doc. Location | Model Output Report
System Description | Residential
SELECT SYSTEM FROM DROP DOWN LIST IN CELL BELOW
System Designation(s)
# of Similar Systems
Total Cooling Capacity |  | kBTU/h |  | kBTU/h
*Table 6.8.1 Unitary Cooling Capacity Range |  | kBTU/h |  | kBTU/h
*Unitary Cooling Eff. (EER or SEER) |  | EER |  | SEER
*Unitary Cooling Part-load Eff. (if applicable) |  | IEER |  | IEER
Total Heating Capacity |  | kBtu/h |  | kBtu/h
*Table 6.8.1 Unitary Heating Capacity Range |  | COP
*Unitary Heating Efficiency
*Fan Control
Supply Airflow |  | cfm |  | cfm
Outdoor Airflow |  | cfm |  | cfm
*Demand Control Ventilation
*Economizer High-Limit Shutoff (°F)
Exhaust Air Energy Recovery Systems
*Exhaust Air Energy Recovery Effectiveness
Supply Fan Power |  | kW |  | kW
Return/Relief Fan Power |  | kW |  | kW
Exhaust Fan Power |  | kW |  | kW
System Fan Power |  | kW |  | kW
Allowed Fan Power: |  | kW |  | kW
Other (describe)
Other (describe)
Other (describe)
Other (describe)

## 6i. HVAC Air-Side (2)
Air-Side HVAC Systems
| HVAC System / Group (BASELINE DESIGN) |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Supporting Doc. Location | Model Output Report
System Description | Nonresidential - < 5 floors and 25,000 - 150,000 ft2
SELECT SYSTEM FROM DROP DOWN LIST IN CELL BELOW
System 4: Packaged VAV with reheat
System Designation(s)
# of Similar Systems
Total Cooling Capacity |  | kBTU/h |  | kBTU/h
*Table 6.8.1 Unitary Cooling Capacity Range |  | kBTU/h |  | kBTU/h
*Unitary Cooling Eff. (EER or SEER) |  | EER |  | SEER
*Unitary Cooling Part-load Eff. (if applicable) |  | IEER |  | IEER
Total Heating Capacity |  | kBtu/h |  | kBtu/h
*Table 6.8.1 Unitary Heating Capacity Range |  | COP
*Unitary Heating Efficiency
*Fan Control
Supply Airflow |  | cfm |  | cfm
Outdoor Airflow |  | cfm |  | cfm
*Demand Control Ventilation
*Economizer High-Limit Shutoff (°F)
Exhaust Air Energy Recovery Systems
*Exhaust Air Energy Recovery Effectiveness
Supply Fan Power |  | kW |  | kW
Return/Relief Fan Power |  | kW |  | kW
Exhaust Fan Power |  | kW |  | kW
System Fan Power |  | kW |  | kW
Allowed Fan Power: |  | kW |  | kW
Other (describe)
Other (describe)
Other (describe)
Other (describe)

## 6j. HVAC Water-side CHW
Chilled Water
Model Input Parameter | HVAC System / Group (BASELINE DESIGN) |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Supporting Doc. Location | Model Output Report
# and Type of Chillers (and capacity of chiller if more than 1 type or size) |  |  | Air cooled w/ 30% propylene glycol solution in primary loop
Total Chiller Capacity
Chiller Efficiency - Full Load |  |  | 1.297 | kW/ton
Chiller Efficiency - Part Load |  |  | 0.884 | kW/ton
Chilled Water (CHW) Supply Temp |  | °F | 44 | °F
CHW ΔT |  | °F | 12 | °F
CHW Supply Temp Reset Parameters |  |  | Demand Reset
CHW Loop Configuration
Number of Primary CHW Pumps |  | # |  | #
Primary CHW Pump Power
Primary CHW Pump Flow |  | gpm |  | gpm
Primary CHW Pump Control
Number of Secondary CHW Pumps |  | # |  | #
Secondary CHW Pump Power
Secondary CHW Pump Flow |  | gpm |  | gpm
Secondary CHW Pump Control
Water-Side Economizer
Water-Side Energy Recovery
Other (describe)
Other (describe)
Other (describe)
Other (describe)

## 6j. HVAC Water-side CW&CT
Cooling Tower & Condenser Water
Model Input Parameter | HVAC System / Group (BASELINE DESIGN) |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Supporting Doc. Location | Model Output Report
Number of Cooling Towers/Fluid Coolers
Cooling Tower Fan Power
Cooling Tower Fan Control
Condenser Water (CW) Leaving Temp |  | °F |  | °F
CW ΔT |  | °F |  | °F
CW Loop Temp Reset Parameters
Number of CW Pumps |  | # |  | #
CW Pump Power
CW Pump Flow |  | gpm |  | gpm
CW Pump Control
Other (describe)
Other (describe)
Other (describe)
Other (describe)

## 6l. HVAC Water-side HW&Steam
Hot Water or Steam
Model Input Parameter | HVAC System / Group (BASELINE DESIGN) |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Supporting Doc. Location | Model Output Report
Number and Type of Boilers | Gas Fired, Hot Water |  | Modulating Condensing w/ 30% propylene glycol solution in primary loop
Total Boiler Capacity |  | kBTU |  | kBTU
Boiler Efficiency |  |  | 93% (@RWT=120°F) 86% (@RWT=140°F) | %
Hot Water or Steam (HHW) Supply Temp | SWT=180°F @ OAT≤20°F SWT=150 °F @ OAT≥50°F | °F | RWT=140°F @ OAT≤20°F RWT=120 °F @ OAT≥50°F | °F
HHW ΔT | 50 | °F | 40 | °F
HHW Temp Reset Parameters | Outdoor air – supply water temp reset |  | Outdoor air – return water temp reset
HHW Loop Configuration |  |  | Primary Only
Number of Primary HHW Pumps |  | # |  | #
Primary HHW Pump Power |  |  | 19 | W/GPM
Primary HHW Pump Flow |  | gpm |  | gpm
Primary HHW Pump Control
Number of Secondary HHW Pumps |  | # |  | #
Secondary HHW Pump Power
Secondary HHW Pump Flow |  | gpm |  | gpm
Secondary HHW Pump Control
Other (describe)
Other (describe)
Other (describe)
Other (describe)

## 6m. HVAC- Geothermal
Geothermal Systems
Model Input Parameter | HVAC System / Group (BASELINE DESIGN) |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Supporting Doc. Location | Model Output Report
Type of Geothermal system | NA
Soil Conductivity (if applicable) | NA
Geothermal source design temperature - summer | NA |  |  | °F
Geothermal source design temperature - winter | NA |  |  | °F
Geoexchange loop design fluid supply temperature - cooling | NA |  |  | °F
Geoexchange loop design fluid supply temperature -heating | NA |  |  | °F
Geoexchange loop - operating temperature | NA
Geothermal energy transfer effect | NA
Geothermal Loop Pumping Configuration | NA
Number of Geothermal Loop Pumps | NA |  |  | #
Geothermal Loop Pump Control | NA
Geothermal Pump Power | NA |  |  | W/gpm
Geothermal Loop Flow | NA |  |  | gpm
Geothermal Air-side Efficiency curves | NA
Other (describe) | NA
Other (describe) | NA
Other (describe) | NA
Other (describe) | NA

## 6n. CHP
Combined Heat & Power Systems
Model Input Parameter | HVAC System / Group (BASELINE DESIGN) |  | HVAC System / Group (PROPOSED DESIGN)
| Description | Units | Description | Units | Supporting Doc. Location | Model Output Report
CHP: Type of generator | NA
Quantity of CHP generators | NA
Total capacity of CHP generators (kW) at design conditions | NA |  |  | kW
CHP: Thermal efficiency (%) at design conditions | NA |  |  | %
CHP: Electrical efficiency (%) at design conditions | NA |  |  | %
CHP: Controls / Schedule | NA
CHP: Fuel Source | NA
CHP: Where is the recovered heat used? (e.g. gas absorption chillers, hot water distribution loop, etc.) | NA
CHP: Backup heat source when waste heat from CHP is unavailable? (e.g. fossil fuel boilers) | NA
CHP: Parasitic losses (e.g. air handling unit to cool the intake air) | NA
Other (describe) | NA
Other (describe) | NA
Other (describe) | NA
Other (describe) | NA